## Sheet1
Theme | Sub-Theme | Document Heading Number | Article / Heading | Table Number | Parameter | Parameter in RfG | Consultation Proposal | Article Number | Type Applicability | Justification Code | Comment
Frequency | N/A | 4.1.1 | Frequency Ranges | 2 | Frequency rangees | 48,5 Hz-49,0 Hz for a time to be specified by each TSO, but not less than 90 minutes | 90 Minutes | 12.1 | TCDF, TC distribution facilities, and TCDS | 2
Voltage | General voltage requirements | 4.2.1.2 | Automatic disconnection due to voltage level | 4 | Minimum Voltage below which Module will automatic disconnect | Specified by the TSO | Site specific | 13.6 | TCDF, TC distribution facilities, and TCDS | 1
Voltage | General voltage requirements | 4.2.1.2 | Automatic disconnection due to voltage level | 4 | Maximum Voltage above which Module will automatic disconnect | Specified by the TSO | Site specific | 13.6 | TCDF, TC distribution facilities, and TCDS | 1
Voltage | General voltage requirements | 4.2.1.3 | Distribution systems connected to the transmission system | 5 | Voltage range | Specified by the TSO | 0.94 pu to 1.06pu | 13.7 | TCDS (with connection point voltage of less 110 kV). | 3
Voltage | General voltage requirements | 4.2.2.1 | Maximum Short-Circuit Current at the connection point | 6 | Maximum Short-Circuit Circuit at 110 kV | Not specified | 110 kV 40 kA 275 kV 50 kA 400 kV 50 kA | 14.1 | TCDF, TCDS | 1
Voltage | General voltage requirements | 4.2.2.2 | Threshold for TSO Report Obligation for change in maximum short-circuit current after unplanned event | 7 | Threshold of the maximum short circuit current inducing an information from the TSO in case of a change above this threshold | Not specified | Specified by TCDF or TCDS | 14.3 | TCDF, TCDS | 3
Voltage | General voltage requirements | 4.2.2.3 | Threshold for TSO Report Obligation for change in maximum short-circuit current after planned event | 8 | Threshold of the maximum short circuit current inducing an information from the TSO in case of a change above this threshold | Not specified | Specified by TCDF or TCDS | 14.5 | TCDF, TCDS | 3
Voltage | General voltage requirements | 4.2.2.4 | Threshold for customer report obligation for change in maximum short-circuit current contribution after an unplanned event | 9 | Threshold of the maximum short circuit current inducing an information from the TCDF or TCDS in case of a change above this threshold | Not specified | 0.5kA | 14.8 | TCDF, TCDS | 3
Voltage | General voltage requirements | 4.2.2.5 | Threshold for customer report obligation for change in maximum short-circuit current contribution after an planned event | 10 | Threshold of the maximum short circuit current inducing an information from the TSO in case of a change above this threshold | Not specified | 0.5kA | 14.9 | TCDF, TCDS | 3
Voltage | Reactive Power Requirements | 4.2.3.1 | Reactive Power Capability for Transmission-Connected Demand Facilities | 11 | Definition of the actual reactive power range for TCDF without onsite generation | consumption: Qmin/Pmax = -0.48 | consumption: Qmin/PMIC = -0.48 | 15.1 (a) | TCDF | 2
Voltage | Reactive Power Requirements | 4.2.3.1 | Reactive Power Capability for Transmission-Connected Demand Facilities | 11 | Definition of the actual reactive power range for TCDF without onsite generation | production: Qmax/Pmax = 0.48 | production: Qmax/PMIC = 0.0 | 15.1 (a) | TCDF | 2
Voltage | Reactive Power Requirements | 4.2.3.1 | Reactive Power Capability for Transmission-Connected Demand Facilities | 11 | Definition of the actual reactive power range for TCDF with onsite generation | consumption: Qmin/Pmax = - 0.48 | consumption: Qmin/max{PMEC,PMIC} = -0.48 | 15.1 (a) | TCDF | 3
Voltage | Reactive Power Requirements | 4.2.3.1 | Reactive Power Capability for Transmission-Connected Demand Facilities | 11 | Definition of the actual reactive power range for TCDF with onsite generation | production: Qmax/Pmax = 0.48 | production: Qmax/Pmax,MEC = 0.48 | 15.1 (a) | TCDF | 3
Voltage | Reactive Power Requirements | 4.2.3.2 | Reactive Power Capability for Transmission-Connected Distribution Systems | 12 | Definition of the actual reactive power range for TCDS during reactive power import | consumption: Qmin/Pmax = -0.48 | consumption: Qmin/max{PMEC,PMIC} = -0.48 | 15.1 (b) | TCDS | 3
Voltage | Reactive Power Requirements | 4.2.3.2 | Reactive Power Capability for Transmission-Connected Distribution Systems | 12 | Definition of the actual reactive power range for TCDS during reactive power export | production: Qmax/Pmax = 0.48 | production: Qmax/PMEC = 0.48 | 15.1 (b) | TCDS | 3
Voltage | Reactive Power Requirements | 4.2.3.3 | Alternative Metrics to Set Out the equivalent reactive range | 13 | Metrics to Express Reactive Power Capability | Not specified | In addition to the power factor, all limits are also expressed as the ratio of Q/Pmax. (with Pmax as either maximum import capacity or maximum export capacity) | 15.1 (d) | TSO | 3
Voltage | Reactive Power Requirements | 4.2.3.4 | Reactive Power Requirments below 25% of Maximum Import Capability | 14 | No reactive power export when at an active power flow of below 25% of maximum import capability | TSO have the right to specify | TCDS shall have the capability to avoid reactive power export at an active power flow of less than 25%PMIC or as result of joint study with TCDS | 15.2 | TCDS | 3
Voltage | Reactive Power Requirements | 4.2.3.5 | Active control of the exchange of reactive power at the connection point of a transmission-connected distribution system | 15 | Active control of the exchange of reactive power at the connection point | TSO have the right to specify | site-specific | 15.3 | TCDS | 3
Voltage | Reactive Power Requirements | 4.2.3.5 | Active control of the exchange of reactive power at the connection point of a transmission-connected distribution system | 15 | Reactive Power management | DSO to request | site-specific | 15.4 | TCDS | 3
Voltage | Reactive Power Requirements | 4.2.4.1 | Power Quality | 16 | Level of voltage distortion or fluctuation of the supply voltage at the connection point | Not specified | ENA G5/4-1 (Harmonics) ENA P28 (Voltage fluctuation) | 20 | TCDF, TCDSO | 1
Demand Response Control | Provision for Demand Units with Demand Response Active Power Control, Reactive Power Control and Transmission Constraint Management | 4.3.1.3 | Demand response active power, reactive power control and transmission constriant management | 19 | Capability to operate across normal voltage range at the connection point specified by the RSO | Not specified | 0.94pu to 1.06pu. LV connected : 0.94pu to 1.1pu. | 28.2(c) | DU offering DR | 1
Demand Response Control | Provision for Demand Units with Demand Response Active Power Control, Reactive Power Control and Transmission Constraint Management | 4.3.1.4 | Demand response active power, reactive power control and transmission constriant management | 20 | Technical specification for the exchange of information | Not specified | TSO will make public all technical specifications to enable the transfer of information available for transmission -connected demand units DSO will make public all technical specifications to enable the transfer of information available for Distribution- connected demand units | 28.2(e) and (l) | DUs | 3
Demand Response Control | Provision for Demand Units with Demand Response Active Power Control, Reactive Power Control and Transmission Constraint Management | 4.3.1.5 | Demand response active power, reactive power control and transmission constriant management | 21 | Definition of the period to adjust power consumption within agreed limits. | Not specified | Be capable of adjusting power consumption within a time period specified and within the limits agreed with the DFO or CDSO. To be agreed on a site specific basis. | 28.2(f) and (j) | DUs | 3
Demand Response Control | Provision for Demand Units with Demand Response Active Power Control, Reactive Power Control and Transmission Constraint Management | 4.3.1.6 | Demand response active power, reactive power control and transmission constriant management | 22 | Definition of the modalities of notification in case of a modification of the DR capability | Not specified | RSO or TSO shall specify the modalities of the notification of modifications of demand response capacity | 28.2(i) | DUs | 3
Demand Response Control | Provision for Demand Units with Demand Response Active Power Control, Reactive Power Control and Transmission Constraint Management | 4.3.1.7 | Demand response active power, reactive power control and transmission constriant management | 23 | Definition of maximum RoCoF | Not specified | 1 Hz/s over 500 ms | 28.2(k) | DUs | 1
Demand Response Control | Specific provision for Demand Units with Frequency Control | 4.3.2.3 | Frequency Control | 26 | Capability to operate across normal voltage range at the connection point specified by the RSO | Not specified | HV Connected: 0.94pu to 1.06pu. LV connected : 0.94pu to 1.1pu. | 29.2(c) | DU offering DR | 1
Demand Response Control | Specific provision for Demand Units with Frequency Control | 4.3.2.4 | Frequency Control | 27 | Define the insensitive dead band around the nominal system frequency | Not Specified | 49.5Hz – 50.2Hz | 29.2 (d) | DU offering DR | 3
Demand Response Control | Specific provision for Demand Units with Frequency Control | 4.3.2.5 | Frequency Control | 28 | Define the maximum frequency deviation from which to respond | Not Specified | Under Frequency maximum frequency deviation – 48.9Hz Over Frequency maximum frequency deviation – 51.1Hz | 29.2(e) | DU offering DR | 3
Demand Response Control | Specific provision for Demand Units with Frequency Control | 4.3.2.6 | Frequency Control | 29 | Specify rapid detection and response requirements | Not specified | Rapid detection and response constitutes an initial time delay of active power response of 0 seconds There should be no delays other than those inherent in the design of the DRSFC system | 29.2 (g) | DU offering DR | 3
Demand Response Control | Specific provisions for Demand Units with Demand Response Very Fast Active Power Control | 4.3.3.1 | Demand Units with demand response very fast active power control | 30 | Provision of Demand response very fast active power control | N/A | To be agreed on an individual contract basis | 30.1 | DFO, CDSO | 1
Demand Response Control | Specific provisions for Demand Units with Demand Response Very Fast Active Power Control | 4.3.3.1 | Demand Units with demand response very fast active power control | 30 | Change of active power | Not specified | To be agreed on an individual contract basis | 30.2(a) | DFO, CDSO | 1
Demand Response Control | Specific provisions for Demand Units with Demand Response Very Fast Active Power Control | 4.3.3.1 | Demand Units with demand response very fast active power control | 30 | Operating principle of control | Not specified | To be agreed on an individual contract basis | 30.2(b) | DFO, CDSO | 1
Demand Response Control | Specific provisions for Demand Units with Demand Response Very Fast Active Power Control | 4.3.3.1 | Demand Units with demand response very fast active power control | 30 | Respond time | Less than 2 sec | 2 seconds or less | 30.2(c) | DFO, CDSO | 1
System Restoration | Low Frequency disconnection | 4.4.1 | Low Frequency disconnection | 31 | Definition of the capabilities of the low frequency demand disconnection scheme | Not specified | 49.5 – 47.0 Hz | 19.1(a) | TCDF, TCDS | 2
System Restoration | Low Frequency disconnection | 4.4.1 | Low Frequency disconnection | 31 | Specification of the proportion of demand | Not specified | For TCDF, up to 100 % of the demand For TCDS, the proportion of demand agreed between the TSO and DSO. | 19.1(a) | TCDF, TCDS | 2
System Restoration | Low Frequency disconnection | 4.4.1 | Low Frequency disconnection | 31 | Use of combination of frequency and RoCoF thresholds for low frequency demand disconnection | Not specified | Not invoking | 19.1(a) | TCDF, TCDS | N/A
System Restoration | Low Frequency disconnection | 4.4.2 | Low Frequency disconnection | 32 | Definition of the capabilities of the low voltage demand disconnection scheme | Not Specified | Site Specific | 19.2(a) | TCDS, TC distribution facilities | 1
System Restoration | Low Frequency disconnection | 4.4.2 | Low Frequency disconnection | 32 | Definition of the capabilities of the low voltage demand disconnection scheme | Not specified | Site Specific | 19.2(b) | TCDF Transmission-connected demand facilities | 1
System Restoration | Low Frequency disconnection | 4.4.2 | Low Frequency disconnection | 32 | On-load tapping changing blocking and Low Voltage demand disconnection (LVDD) | Right to specify or not specify | Right to specify | 19.2(c) and (d) | TCDS | 3
System Restoration | Low Frequency disconnection | 4.4.3 | Low Frequency disconnection | 33 | Definition of the automatic on load tap changer blocking scheme | Right to specify or not specify | Right to specify | 19.3(b) | TC Distribution Facility | 3
System Restoration | Low Frequency disconnection | 4.4.4 | Conditions for reconnection post disconnection | 34 | Definition of the conditions for reconnection post disconnection | Not specified | To be specified as part of the System defence and/or System Restoration Plans | 19.4(a) | TCDF, TCDS | 3
System Restoration | Low Frequency disconnection | 4.4.4 | Conditions for reconnection post disconnection | 34 | Settings of the synchronisation devices( including frequency, voltage, phase angle range and deviation of voltage and frequency) | Not specified | Site specific | 19.4(b) | TCDF, TCDS | 1
System Restoration | Low Frequency disconnection | 4.4.4 | Conditions for reconnection post disconnection | 34 | Specification of the time required for remote disconnection | Not specified | 0 Secs No time delays other inherent in the design of the relevant systems | 19.4(c) | TCDF, TCDS | 3
System Restoration | Low Frequency disconnection | 4.4.4 | Conditions for reconnection post disconnection | 34 | Automated disconnection equipment for reconfiguration in preparation for block loading | Not specific | Site specific | 19.4(c) | TCDF, TCDS | 3
Instrumentation, Simulation and Control Theme | Electrical Protection Schemes and Settings | 4.5.1 | Electrical protection schemes and settings | 35 | Electrical protection schemes and settings | Not specific | Site specific | 16.1 | TCDF, TCDS | 1
Instrumentation, Simulation and Control Theme | Electrical Protection Schemes and Settings | 4.5.2 | Specification and Agreement of control Schemes and settings | 36 | Specification and agreement of control schemes and settings | Not specific | Site specific | 17.1 | TCDF, TCDS | 1
Instrumentation, Simulation and Control Theme | Information exchange | 4.5.3 | Information exchange | 37 | Specification of information exchange standards | Not specific | The publication of the necessary standards to SONI Website | 18.3 | TSO | 3
Instrumentation, Simulation and Control Theme | Content and format of simulation models | 4.5.4 | Content and format of simulation models | 38 | Content and format of simulation models | To include: - Steady and dynamic states, including 50 Hz component; -Electromagnetic transient simulations at the connection point; -Structure and block diagrams. | The provided simulation models must include the following a. Steady and dynamic states, including 50 Hz component, suitable for loadflow, fault level analysis (balanced and unbalanced faults) and RMS dynamic simulations; b. Electromagnetic transient simulations at the connection point; c. Structure and block diagrams. d. Harmonics, including harmonic impedance and harmonic emissions | 21.3 | TCDF, TCDS | 1
Instrumentation, Simulation and Control Theme | Recording requirements for comparison with simulation mondels | 4.5.5 | Recording requirements for comparison with simulation mondels | 39 | Recording requirements | Not specified | Application - specific | 21.5 | TCDFs,TCDSs | 1