## Ireland
Theme | Sub-Theme | Document Heading Number | Article / Heading | Table Number | Parameter | Parameter in RfG | Consultation Proposal | Article Number | Type Applicability | Justification Code | Parameter or Requirement | Comment
Frequency Theme | Frequency ranges | 4.1.1.1 | Article 13.1 (a) (i): Frequency Ranges | 2 | Frequency Ranges | 48,5 Hz-49,0 Hz for a time to be specified by each TSO, but not less than 90 minutes | 90 Minutes | 13.1.a.(i) | A, B, C, D PGMs and Offshore PPMs | 2 | parameter
Frequency Theme | Rate of Change of Frequency | 4.1.2.1 | Article 13.1 (b): RoCoF | 3 | The maximum RoCoF for which the Power Generating Module (PGM) shall stay connected | Not Specified | 1 Hz/s over 500ms window | 13.1.b | A, B, C and D PGMs and Offshore PPMs | 1 | parameter
Frequency Theme | Rate of Change of Frequency | 4.1.2.1 | Article 13.1 (b): RoCoF | 4 | The proposal for loss of mains protection (Transmission Connected) | Not Specified | 1 Hz/s over 500ms window | 13.1.b | A, B, C and D and Offshore PPMs | 1 | parameter
Frequency Theme | Rate of Change of Frequency | 4.1.2.1 | Article 13.1 (b): RoCoF | 5 | The proposal for loss of mains protection (Distribution Connected) | Not Specified | DFIG / Full Converter Generator 2 Hz/s 0.3s Synchronous Generator / Directly Connected Induction Generator H > 3 MWs/MVA 0.6 Hz/s 0.6s Synchronous Generator / Directly Connected Induction Generator H ≤ 3 MWs/MVA 1.0 Hz/s 0.6s | 13.1.b | A, B, C and D and Offshore PPMs | 1 | parameter
Frequency Theme | Active Power Control | 4.1.3.1 | Article 13.4.a: Admissible reduction from maximum output with falling frequency | 6 | Admissible active power reduction from maximum output with falling frequency | below 49 Hz falling by a reduction rate of 2% of the maximum capacity at 50 Hz per 1 Hz frequency drop or below 49.5 Hz falling by a reduction rate of 10% of the maximum capacity at 50 Hz per 1 Hz frequency drop. | below 49 Hz falling by a reduction rate of 2% of the maximum capacity at 50 Hz per 1 Hz frequency drop | 13.4 (a) | A, B, C and D PGMs and Offshore PPMs | 3 | parameter
Frequency Theme | Active Power Control | 4.1.3.2 | Article 13.5: Admissible reduction from maximum output with falling frequency taking Account of Technical Capabilities of PGMs | 7 | Ambient Conditions | Not Specified | 10°C, 70% relative humidity and 1013 hPa for gas fired turbine generators | 13.5 | Gas-fired SPGMs (A, B, C and D). | 3 | parameter
Frequency Theme | Active Power Control | 4.1.3.3 | Article 13.6: Remote operation of facility to cease active power output | 8 | Specify requirements for equipment to make this facility operable remotely for Type A | A right to specify | Maintain the right to specify for Type A only in due time for plant design (c/f Art 14 (2) (b) for Type B | 13.6 | A PGMs | 3 | requirement
Frequency Theme | Active Power Control | 4.1.3.4 | Article 13.7: Automatic connection to the network | 9 | (i) Frequency Ranges and Time Delay | Non-specific | 49.8 Hz to 50.2 Hz with a five minute delay | 13.7 | A, B and C PGMs | 1 | parameter
Frequency Theme | Active Power Control | 4.1.3.4 | Article 13.7: Automatic connection to the network | 9 | (ii) Maximum admissible gradient of increase in power | Non-specific | 10% of Pmax per minute | 13.7 | A, B and C PGMs | 1 | parameter
Frequency Theme | Active Power Control | 4.1.3.4 | Article 13.7: Automatic connection to the network | 9 | (iii) Allowing automatic connection | A right to not allow | Allow | 13.7 | A, B and C PGMs | 1 | parameter
Frequency Theme | Active Power Control | 4.1.3.5 | Article 14.2.b: Remote operation of power output | 10 | Right to specify the requirements for further equipment to allow active power output to be remotely operated | To specify or not to specify | RSO to specify for Type B generators with a maximum capacity 1 MW and above; in due time for plant design. | 14.2 (b) | B PGMs | 3 | requirement
Frequency Theme | Active Power Control | 4.1.3.6 | Article 15.2.a: Achieving Active Power Set points | 11 | The period within which the adjusted active power setpoint must be reached | No range provided | 10 seconds response time plus the ramp rate for the unit. NB where wind turbines have to be turned on to achieve the set point then a maximum of 3 minutes response time is allowed. | 15.2 (a) | C and D PGMs | 1 | parameter
Frequency Theme | Active Power Control | 4.1.3.6 | Article 15.2.a: Achieving Active Power Set points | 11 | Tolerance (subject to the availability of the prime mover resource) applying to the new setpoint and the time within which it must be reached | No Range Provided | For PGMs, the maximum of 1 MW or 1% of dispatch quantity is applied. For PPMs, the maximum of +/- 3% of registered capacity or +/- 0.5 MW. | 15.2 (a) | C and D PGMs | 3 | parameter
Frequency Theme | Frequency Modes | 4.1.4.2 | Article 13.2.a: LFSM-O Parameter Selection | 12 | Frequency threshold | Between 50.2- 50.5 Hz | 50.2 Hz | 13.2(a) | A, B, C and D PGMs & offshore PPMs | 2 | parameter
Frequency Theme | Frequency Modes | 4.1.4.2 | Article 13.2.a: LFSM-O Parameter Selection | 12 | Droop settings | Between 2-12 % | Machines should be capable of operating in the range 2-12%. The default setting is 4% | 13.2(a) | A, B, C and D PGMs & offshore PPMs | 2 | parameter
Frequency Theme | Frequency Modes | 4.1.4.3 | Article 13.2.b: LFSM-O: Automatic disconnection and reconnection | 13 | Automatic disconnection and reconnection of PGMs | Allow or do not allow | Do not allow | 13.2 (b) | A PGMs | 3 | requirement
Frequency Theme | Frequency Modes | 4.1.4.4 | Article 13.2.f: LFSM-O: Actions at minimum regulating level | 14 | Actions in LFSM-O upon reaching minimum regulating level, | Choose between (i) continuing operation at this level; or (ii) further decreasing active power output | (i) continuing operation at this level | 13.2 (f) | A, B, C and D PGMs & offshore PPMs | 1 | requirement
Frequency Theme | Frequency Modes | 4.1.4.5 | Article 15.2.c: LFSM-U Parameter Selection | 15 | Frequency threshold | between 49.8 Hz and 49.5 Hz inclusive | 49.5 Hz | 15.2 (c) | C and D PGMs & offshore PPMs | 1 | parameter
Frequency Theme | Frequency Modes | 4.1.4.5 | Article 15.2.c: LFSM-U Parameter Selection | 15 | Droop settings | 2-12% | Default is 4% unless otherwise specified by the TSO on a site specific basis | 15.2 (c) | C and D PGMs & offshore PPMs | 1 | parameter
Frequency Theme | Frequency Modes | 4.1.4.6 | Article 15.2.d.(i) and (ii): FSM Parameter Selection | 16 | Active Power Range (ΔP/Pmax) | 1.5-10% | Not proposing a value at this time | 15.2 (d) (i) and (ii) | C and D PGMs & offshore PPMs | 1 | parameter
Frequency Theme | Frequency Modes | 4.1.4.6 | Article 15.2.d.(i) and (ii): FSM Parameter Selection | 16 | Frequency Response Insensitivity (Δf) | 10-30 mHz | 15mHz | 15.2 (d) (i) and (ii) | C and D PGMs & offshore PPMs | 3 | parameter
Frequency Theme | Frequency Modes | 4.1.4.6 | Article 15.2.d.(i) and (ii): FSM Parameter Selection | 16 | Frequency Response Insensitivity (Δf/f) | 0.02-0.06% | 0.03% | 15.2 (d) (i) and (ii) | C and D PGMs & offshore PPMs | 3 | parameter
Frequency Theme | Frequency Modes | 4.1.4.6 | Article 15.2.d.(i) and (ii): FSM Parameter Selection | 16 | Frequency Response Deadband | 0-500mHz | +/-15mHz | 15.2 (d) (i) and (ii) | C and D PGMs& offshore PPMs | 3 | parameter
Frequency Theme | Frequency Modes | 4.1.4.6 | Article 15.2.d.(i) and (ii): FSM Parameter Selection | 16 | Droop | 2-12% | Depends on gen type – default is 4% | 15.2 (d) (i) and (ii) | C and D PGMs & offshore PPMs | 1 | parameter
Frequency Theme | Frequency Modes | 4.1.4.7 | Article 15.2.d.(iii): FSM: Step Change in Frequency | 17 | Active power range | 1.5-10% | 5% | 15.2 (d) (iii) | C and D PGMs & offshore PPMs | 3 | parameter
Frequency Theme | Frequency Modes | 4.1.4.7 | Article 15.2.d.(iii): FSM: Step Change in Frequency | 17 | Admissible initial time delay for activation of active power frequency response for PPMs | Less than 2 seconds | 0s No time delays other than those inherent in the design of the frequency response system | 15.2 (d) (iii) | C and D PGMs & offshore PPMs | 3 | parameter
Frequency Theme | Frequency Modes | 4.1.4.7 | Article 15.2.d.(iii): FSM: Step Change in Frequency | 17 | Maximum admissible choice of full activation time | 30 seconds | 5s | 15.2 (d) (iii) | C and D PGMs & offshore PPMs | 3 | parameter
Frequency Theme | Frequency Modes | 4.1.4.7 | Article 15.2.d.(iii): FSM: Step Change in Frequency | 17 | Capability relating to the duration of provision of full active power frequency response | 15-30 minutes | 20 min | 15.2 (d) (v) | C and D PGMs & offshore PPMs | 3 | parameter
Frequency Theme | Non-Mandatory Frequency Requirements that we are not invoking at this time | 4.1.5 | Non-Mandatory Frequency Requirements that we are not invoking at this time | 18 | Shorter initial FSM response delay for PGMs without inertia | Not specified | Not Mandatory – can be agreed on a case by case basis with System Services Contracts | 15.2.d(iv) | Type A, B, C and D PGMs and offshore PPMs | N/A | requirement
Frequency Theme | Non-Mandatory Frequency Requirements that we are not invoking at this time | 4.1.5 | Non-Mandatory Frequency Requirements that we are not invoking at this time | 18 | Synthetic inertia capability for PPM | Not Specified | Not Mandatory – can be agreed on a case by case basis with System Services Contracts | 21(2) | C and D PPMs | N/A | requirement
Voltage Theme | Automatic Disconnection Due to Voltage Level | 4.2.1.1 | Article 15.3: Type C Automatic Disconnection Due to Voltage Level | 19 | Minimum Voltage below which Module will automatic disconnect | Not specified | 0.87 p.u. & 3s | 15.3 | C (PPM) | 1 | parameter
Voltage Theme | Automatic Disconnection Due to Voltage Level | 4.2.1.1 | Article 15.3: Type C Automatic Disconnection Due to Voltage Level | 19 | Minimum Voltage below which Module will automatic disconnect | Not specified | 0.8 p.u. & 1.1s | 15.3 | C (PPM) | 1 | parameter
Voltage Theme | Automatic Disconnection Due to Voltage Level | 4.2.1.1 | Article 15.3: Type C Automatic Disconnection Due to Voltage Level | 19 | Minimum Voltage below which Module will automatic disconnect | Not specified | 0.87 p.u. & 2.5s | 15.3 | C (SPGM) | 1 | parameter
Voltage Theme | Automatic Disconnection Due to Voltage Level | 4.2.1.1 | Article 15.3: Type C Automatic Disconnection Due to Voltage Level | 19 | Maximum Voltage above which Module will automatic disconnect | Not specified | 0.8 p.u. & 0.7s | 15.3 | C (SPGM) | 1 | parameter
Voltage Theme | Automatic Disconnection Due to Voltage Level | 4.2.1.1 | Article 15.3: Type C Automatic Disconnection Due to Voltage Level | 19 | Maximum Voltage above which Module will automatic disconnect | Not specified | 1.12 p.u. & 0.7s | 15.3 | C PGMs | 1 | parameter
Voltage Theme | Automatic Disconnection Due to Voltage Level | 4.2.1.2 | Article 16.2.c: Type D Automatic Disconnection Due to Voltage Level | 20 | Minimum Voltage below which Module will automatic disconnect | Not specified | Not Allowed | 16.2.c | D PGMs | 3 | parameter
Voltage Theme | Automatic Disconnection Due to Voltage Level | 4.2.1.2 | Article 16.2.c: Type D Automatic Disconnection Due to Voltage Level | 20 | Maximum Voltage above which Module will automatic disconnect | Not specified | Not Allowed | 16.2.c | D PGMs | 3 | parameter
Voltage Theme | Automatic Disconnection Due to Voltage Level | 4.2.1.2 | Article 16.2.c: Type D Automatic Disconnection Due to Voltage Level | 21 | Minimum Voltage below which Module will automatic disconnect | Not specified | 0.87 p.u. & 3s | 15.3 | D(PPM) | 1 | parameter
Voltage Theme | Automatic Disconnection Due to Voltage Level | 4.2.1.2 | Article 16.2.c: Type D Automatic Disconnection Due to Voltage Level | 21 | Minimum Voltage below which Module will automatic disconnect | Not specified | 0.8 p.u. & 1.1s | 15.3 | D(PPM) | 1 | parameter
Voltage Theme | Automatic Disconnection Due to Voltage Level | 4.2.1.2 | Article 16.2.c: Type D Automatic Disconnection Due to Voltage Level | 21 | Minimum Voltage below which Module will automatic disconnect | Not specified | 0.87 p.u. & 2.5s | 15.3 | D (SPGM) | 1 | parameter
Voltage Theme | Automatic Disconnection Due to Voltage Level | 4.2.1.2 | Article 16.2.c: Type D Automatic Disconnection Due to Voltage Level | 21 | Minimum Voltage below which Module will automatic disconnect | Not specified | 0.8 p.u. & 0.7s | 15.3 | D (SPGM) | 1 | parameter
Voltage Theme | Automatic Disconnection Due to Voltage Level | 4.2.1.2 | Article 16.2.c: Type D Automatic Disconnection Due to Voltage Level | 21 | Maximum Voltage above which Module will automatic disconnect | Not specified | 1.12 p.u. & 0.7s | 15.3 | D PGMs | 1 | parameter
Voltage Theme | Reactive Power Capability for Type B PGMs | 4.2.2.1.1 | Article 17.2.a: Reactive Power capability for Type B SPGMs | 22 | right to specify the capability of a synchronous power generating module to provide reactive power; | To specify or not to specify | Maintain existing reactive power requirements in the Distribution Code. | 18.2.a | Type C and D SPGMs | 1 | requirement
Voltage Theme | Reactive Power Capability for Type B PGMs | 4.2.2.1.2 | Article 20.2.a: Reactive Power capability for Type B PPMs | 23 | right to specify the capability of a synchronous power generating module to provide reactive power; | To specify or not to specify | Maintain existing reactive power requirements in the Distribution Code. | 18.2.a | Type C and D SPGMs | 1 | requirement
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.1 | Article 18.2.b.(i): SPGM: Parameters required for U-Q/Pmax Profiles | 24 | umin (110 kV ) | 0.875 p.u. | 0.9 p.u. | 18.2.b (ii) | D SPGMs | 1 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.1 | Article 18.2.b.(i): SPGM: Parameters required for U-Q/Pmax Profiles | 24 | umax (110 kV ) | 1.1 p.u. | 1.1 p.u. | 18.2.b (ii) | D SPGMs | 2 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.1 | Article 18.2.b.(i): SPGM: Parameters required for U-Q/Pmax Profiles | 24 | Qmin/Pmax (lead) (110 kV ) | -0.5 p.u. | -0.5 p.u. | 18.2.b (ii) | D SPGMs | 2 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.1 | Article 18.2.b.(i): SPGM: Parameters required for U-Q/Pmax Profiles | 24 | Qmax/Pmax (lag) (110 kV ) | 0.65 p.u. | 0.52 p.u. | 18.2.b (ii) | D SPGMs | 2 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.1 | Article 18.2.b.(i): SPGM: Parameters required for U-Q/Pmax Profiles | 24 | umin (220 kV) | 0.875 p.u. | 0.9 p.u. | 18.2.b (ii) | D SPGMs | 2 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.1 | Article 18.2.b.(i): SPGM: Parameters required for U-Q/Pmax Profiles | 24 | umax (220 kV) | 1.1 p.u. | 1.1 p.u. | 18.2.b (ii) | D SPGMs | 2 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.1 | Article 18.2.b.(i): SPGM: Parameters required for U-Q/Pmax Profiles | 24 | Qmin/Pmax (lead) (220 kV) | -0.5 p.u. | -0.5 p.u. | 18.2.b (ii) | D SPGMs | 2 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.1 | Article 18.2.b.(i): SPGM: Parameters required for U-Q/Pmax Profiles | 24 | Qmax/Pmax (lag) (220 kV) | 0.65 p.u. | 0.52 p.u. | 18.2.b (ii) | D SPGMs | 2 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.1 | Article 18.2.b.(i): SPGM: Parameters required for U-Q/Pmax Profiles | 24 | umin (400 kV) | 0.875 p.u. | 0.875 p.u. | 18.2.b (ii) | D SPGMs | 1 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.1 | Article 18.2.b.(i): SPGM: Parameters required for U-Q/Pmax Profiles | 24 | umax (400 kV) | 1.1 p.u. | 1.05 p.u. | 18.2.b (ii) | D SPGMs | 1 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.1 | Article 18.2.b.(i): SPGM: Parameters required for U-Q/Pmax Profiles | 24 | Qmin/Pmax (lead) (400 kV) | -0.5 p.u. | -0.5 p.u. | 18.2.b (ii) | D SPGMs | 2 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.1 | Article 18.2.b.(i): SPGM: Parameters required for U-Q/Pmax Profiles | 24 | Qmax/Pmax (lag) (400 kV) | 0.65 p.u. | 0.52 p.u. | 18.2.b (ii) | D SPGMs | 2 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.1 | Article 18.2.b.(i): SPGM: Parameters required for U-Q/Pmax Profiles | 25 | umin (10 kV and 20kV) | 0.875 p.u. | 0.96 p.u. | 18.2.b (ii) | C and D SPGMs | 1 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.1 | Article 18.2.b.(i): SPGM: Parameters required for U-Q/Pmax Profiles | 25 | umax (10 kV and 20kV) | 1.1 p.u. | 1.1 p.u. | 18.2.b (ii) | C and D SPGMs | 2 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.1 | Article 18.2.b.(i): SPGM: Parameters required for U-Q/Pmax Profiles | 25 | Qmin/Pmax (import) (10 kV and 20kV) | -0.5 p.u. | -0.33 p.u. | 18.2.b (ii) | C and D SPGMs | 2 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.1 | Article 18.2.b.(i): SPGM: Parameters required for U-Q/Pmax Profiles | 25 | Qmax/Pmax (Export) (10 kV and 20kV) | 0.65 p.u. | 0 p.u. | 18.2.b (ii) | C and D SPGMs | 2 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.1 | Article 18.2.b.(i): SPGM: Parameters required for U-Q/Pmax Profiles | 25 | umin (38 kV) | 0.875 p.u. | 0.937 p.u. | 18.2.b (ii) | C and D SPGMs | 1 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.1 | Article 18.2.b.(i): SPGM: Parameters required for U-Q/Pmax Profiles | 25 | umax (38 kV) | 1.1 p.u. | 1.1 p.u. | 18.2.b (ii) | C and D SPGMs | 1 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.1 | Article 18.2.b.(i): SPGM: Parameters required for U-Q/Pmax Profiles | 25 | Qmin/Pmax (Import) (38 kV) | -0.5 p.u. | -0.33 p.u. | 18.2.b (ii) | C and D SPGMs | 2 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.1 | Article 18.2.b.(i): SPGM: Parameters required for U-Q/Pmax Profiles | 25 | Qmax/Pmax (Export) (38 kV) | 0.65 p.u. | 0 p.u. | 18.2.b (ii) | C and D SPGMs | 2 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.2 | Article 18.2.b. (iv): SPGM: Time to Achieve Target Value within U-Q/Pmax Profile | 26 | Time to achieve target value [transmission connected] | Not specified | Without undue delay but at least within 120 seconds | 18.2.b (iv) | C and D SPGMs | 1 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.2 | Article 18.2.b. (iv): SPGM: Time to Achieve Target Value within U-Q/Pmax Profile | 26 | Time to achieve target value [distribution connected] | Not specified | Without undue delay but at least within 120 seconds | 18.2.b (iv) | C and D SPGMs | 3 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.3 | Article 21.3.b (i) and (ii) & Article 25.5: PPM: Parameters required for U-Q/Pmax Profiles | 27 | umin (110 kV) | 0.875 p.u. | 0.9 p.u. | 21.3.b (ii) | D PPMs | 1 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.3 | Article 21.3.b (i) and (ii) & Article 25.5: PPM: Parameters required for U-Q/Pmax Profiles | 27 | umax (110 kV) | 1.1 p.u. | 1.1 p.u. | 21.3.b (ii) | D PPMs | 2 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.3 | Article 21.3.b (i) and (ii) & Article 25.5: PPM: Parameters required for U-Q/Pmax Profiles | 27 | Qmin/Pmax (lead) (110 kV) | -0.5 p.u. | -0.33 p.u. | 21.3.b (ii) | D PPMs | 1 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.3 | Article 21.3.b (i) and (ii) & Article 25.5: PPM: Parameters required for U-Q/Pmax Profiles | 27 | Qmax/Pmax (lag) (110 kV) | 0.65 p.u. | 0.33 p.u. | 21.3.b (ii) | D PPMs | 1 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.3 | Article 21.3.b (i) and (ii) & Article 25.5: PPM: Parameters required for U-Q/Pmax Profiles | 27 | umin (220 kV) | 0.875 p.u. | 0.9 p.u. | 21.3.b (ii) | D PPMs | 2 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.3 | Article 21.3.b (i) and (ii) & Article 25.5: PPM: Parameters required for U-Q/Pmax Profiles | 27 | umax (220 kV) | 1.1 p.u. | 1.1 p.u. | 21.3.b (ii) | D PPMs | 2 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.3 | Article 21.3.b (i) and (ii) & Article 25.5: PPM: Parameters required for U-Q/Pmax Profiles | 27 | Qmin/Pmax (lead) (220 kV) | -0.5 p.u. | -0.33 p.u. | 21.3.b (ii) | D PPMs | 1 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.3 | Article 21.3.b (i) and (ii) & Article 25.5: PPM: Parameters required for U-Q/Pmax Profiles | 27 | Qmax/Pmax (lead) (220 kV) | 0.65 p.u. | 0.33 p.u. | 21.3.b (ii) | D PPMs | 1 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.3 | Article 21.3.b (i) and (ii) & Article 25.5: PPM: Parameters required for U-Q/Pmax Profiles | 27 | umin (400 kV) | 0.875 p.u. | 0.875 p.u. | 21.3.b (ii) | D PPMs | 1 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.3 | Article 21.3.b (i) and (ii) & Article 25.5: PPM: Parameters required for U-Q/Pmax Profiles | 27 | umax (400 kV) | 1.1 p.u. | 1.05 p.u. | 21.3.b (ii) | D PPMs | 1 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.3 | Article 21.3.b (i) and (ii) & Article 25.5: PPM: Parameters required for U-Q/Pmax Profiles | 27 | Qmin/Pmax (lead) (400 kV) | -0.5 p.u. | -0.33 p.u. | 21.3.b (ii) | D PPMs | 1 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.3 | Article 21.3.b (i) and (ii) & Article 25.5: PPM: Parameters required for U-Q/Pmax Profiles | 27 | Qmax/Pmax (lag) (400 kV) | 0.65 p.u. | 0.33 p.u. | 21.3.b (ii) | D PPMs | 1 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.3 | Article 21.3.b (i) and (ii) & Article 25.5: PPM: Parameters required for U-Q/Pmax Profiles | 28 | umin (10 kV and 20kV topology 2 ) | 0.875 p.u. | 0.96 p.u. | 21.3.b (ii) | C and D PPM | 1 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.3 | Article 21.3.b (i) and (ii) & Article 25.5: PPM: Parameters required for U-Q/Pmax Profiles | 28 | umax (10 kV and 20kV topology 2 ) | 1.1 p.u. | 1.1 p.u. | 21.3.b (ii) | C and D PPM | 2 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.3 | Article 21.3.b (i) and (ii) & Article 25.5: PPM: Parameters required for U-Q/Pmax Profiles | 28 | Qmin/Pmax (lead) (10 kV and 20kV topology 2 ) | -0.5 p.u. | -0.33 p.u. | 21.3.b (ii) | C and D PPM | 2 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.3 | Article 21.3.b (i) and (ii) & Article 25.5: PPM: Parameters required for U-Q/Pmax Profiles | 28 | Qmax/Pmax (lag) (10 kV and 20kV topology 2 ) | 0.65 p.u. | 0.33 p.u. | 21.3.b (ii) | C and D PPM | 2 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.3 | Article 21.3.b (i) and (ii) & Article 25.5: PPM: Parameters required for U-Q/Pmax Profiles | 28 | umin (38 kV topology 2 ) | 0.875 p.u. | 0.937 p.u. | 21.3.b (ii) | C and D PPM | 1 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.3 | Article 21.3.b (i) and (ii) & Article 25.5: PPM: Parameters required for U-Q/Pmax Profiles | 28 | umax (38 kV topology 2 ) | 1.1 p.u. | 1.1 p.u. | 21.3.b (ii) | C and D PPM | 1 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.3 | Article 21.3.b (i) and (ii) & Article 25.5: PPM: Parameters required for U-Q/Pmax Profiles | 28 | Qmin/Pmax (lead) (38 kV topology 2 ) | -0.5 p.u. | -0.33 p.u. | 21.3.b (ii) | C and D PPM | 2 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.3 | Article 21.3.b (i) and (ii) & Article 25.5: PPM: Parameters required for U-Q/Pmax Profiles | 28 | Qmax/Pmax (lag) (38 kV topology 2 ) | 0.65 p.u. | 0.33 p.u. | 21.3.b (ii) | C and D PPM | 2 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.3 | Article 21.3.b (i) and (ii) & Article 25.5: PPM: Parameters required for U-Q/Pmax Profiles | 29 | umin (10 kV and 20kV all other topologies) | 0.875 p.u. | 0.96 p.u. | 21.3.b (ii) | C and D PPM | 1 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.3 | Article 21.3.b (i) and (ii) & Article 25.5: PPM: Parameters required for U-Q/Pmax Profiles | 29 | umax (10 kV and 20kV all other topologies) | 1.1 p.u. | 1.1 p.u. | 21.3.b (ii) | C and D PPM | 2 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.3 | Article 21.3.b (i) and (ii) & Article 25.5: PPM: Parameters required for U-Q/Pmax Profiles | 29 | Qmin/Pmax (lead) (10 kV and 20kV all other topologies) | -0.5 p.u. | -0.42 p.u. | 21.3.b (ii) | C and D PPM | 2 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.3 | Article 21.3.b (i) and (ii) & Article 25.5: PPM: Parameters required for U-Q/Pmax Profiles | 29 | Qmax/Pmax (lag) (10 kV and 20kV all other topologies) | 0.65 p.u. | 0 p.u. | 21.3.b (ii) | C and D PPM | 2 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.3 | Article 21.3.b (i) and (ii) & Article 25.5: PPM: Parameters required for U-Q/Pmax Profiles | 29 | umin (38 kV all other topologies) | 0.875 p.u. | 0.937 p.u. | 21.3.b (ii) | C and D PPM | 1 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.3 | Article 21.3.b (i) and (ii) & Article 25.5: PPM: Parameters required for U-Q/Pmax Profiles | 29 | umax (38 kV all other topologies) | 1.1 p.u. | 1.1 p.u. | 21.3.b (ii) | C and D PPM | 1 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.3 | Article 21.3.b (i) and (ii) & Article 25.5: PPM: Parameters required for U-Q/Pmax Profiles | 29 | Qmin/Pmax (lead) (38 kV all other topologies) | -0.5 p.u. | -0.42 p.u. | 21.3.b (ii) | C and D PPM | 2 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.3 | Article 21.3.b (i) and (ii) & Article 25.5: PPM: Parameters required for U-Q/Pmax Profiles | 29 | Qmax/Pmax (lag) (38 kV all other topologies) | 0.65 p.u. | 0 p.u. | 21.3.b (ii) | C and D PPM | 2 | parameter
Voltage Theme | Reactive Power Capability below Maximum Capacity: P-Q/Pmax Profiles | 4.2.2.3.1 | Article 21.3.c.(i), (ii) and (iv): PPM: Parameters required for P-Q/Pmax Profiles | 30 | pmin (110 to 400kV ) | 0.0 p.u. | 0.12 p.u. | 21.3.c (ii) | D PPMs | 1 | parameter
Voltage Theme | Reactive Power Capability below Maximum Capacity: P-Q/Pmax Profiles | 4.2.2.3.1 | Article 21.3.c.(i), (ii) and (iv): PPM: Parameters required for P-Q/Pmax Profiles | 30 | pmax (110 to 400kV ) | 1.0 p.u. | 1.0 p.u. | 21.3.c (ii) | D PPMs | 1 | parameter
Voltage Theme | Reactive Power Capability below Maximum Capacity: P-Q/Pmax Profiles | 4.2.2.3.1 | Article 21.3.c.(i), (ii) and (iv): PPM: Parameters required for P-Q/Pmax Profiles | 30 | Qmin/Pmax (lead) (110 to 400kV ) | -0.5 p.u. | -0.33 p.u. | 21.3.c (ii) | D PPMs | 1 | parameter
Voltage Theme | Reactive Power Capability below Maximum Capacity: P-Q/Pmax Profiles | 4.2.2.3.1 | Article 21.3.c.(i), (ii) and (iv): PPM: Parameters required for P-Q/Pmax Profiles | 30 | Qmax/Pmax (lag) (110 to 400kV ) | 0.65 p.u. | 0.33 p.u. | 21.3.c (ii) | D PPMs | 1 | parameter
Voltage Theme | Reactive Power Capability below Maximum Capacity: P-Q/Pmax Profiles | 4.2.2.3.1 | Article 21.3.c.(i), (ii) and (iv): PPM: Parameters required for P-Q/Pmax Profiles | 31 | pmin (10kV, 20kV or 38kV topology 2) | 0.0 p.u. | 0.12 p.u. | 21.3.c (ii) | C and D PPM | 1 | parameter
Voltage Theme | Reactive Power Capability below Maximum Capacity: P-Q/Pmax Profiles | 4.2.2.3.1 | Article 21.3.c.(i), (ii) and (iv): PPM: Parameters required for P-Q/Pmax Profiles | 31 | pmax (10kV, 20kV or 38kV topology 2) | 1.0 p.u. | 1.0 p.u. | 21.3.c (ii) | C and D PPM | 1 | parameter
Voltage Theme | Reactive Power Capability below Maximum Capacity: P-Q/Pmax Profiles | 4.2.2.3.1 | Article 21.3.c.(i), (ii) and (iv): PPM: Parameters required for P-Q/Pmax Profiles | 31 | Qmin/Pmax (lead) (10kV, 20kV or 38kV topology 2) | -0.5 p.u. | -0.33 p.u. | 21.3.c (ii) | C and D PPM | 1 | parameter
Voltage Theme | Reactive Power Capability below Maximum Capacity: P-Q/Pmax Profiles | 4.2.2.3.1 | Article 21.3.c.(i), (ii) and (iv): PPM: Parameters required for P-Q/Pmax Profiles | 31 | Qmax/Pmax (lag) (10kV, 20kV or 38kV topology 2) | 0.65 p.u. | 0.33 p.u. | 21.3.c (ii) | C and D PPM | 1 | parameter
Voltage Theme | Reactive Power Capability below Maximum Capacity: P-Q/Pmax Profiles | 4.2.2.3.1 | Article 21.3.c.(i), (ii) and (iv): PPM: Parameters required for P-Q/Pmax Profiles | 32 | pmin (10kV, 20kV or 38kV Topology 3 & 4) | 0.0 p.u. | 0.12 p.u. | 21.3.c (ii) | C and D PPM | 1 | parameter
Voltage Theme | Reactive Power Capability below Maximum Capacity: P-Q/Pmax Profiles | 4.2.2.3.1 | Article 21.3.c.(i), (ii) and (iv): PPM: Parameters required for P-Q/Pmax Profiles | 32 | pmax (10kV, 20kV or 38kV Topology 3 & 4) | 1.0 p.u. | 1.0 p.u. | 21.3.c (ii) | C and D PPM | 1 | parameter
Voltage Theme | Reactive Power Capability below Maximum Capacity: P-Q/Pmax Profiles | 4.2.2.3.1 | Article 21.3.c.(i), (ii) and (iv): PPM: Parameters required for P-Q/Pmax Profiles | 32 | Qmin/Pmax (lead) (10kV, 20kV or 38kV Topology 3 & 4) | -0.5 p.u. | Power factor range from 0.92 [-0.42 Q / Pmax] to unity [0 Q/Pmax] | 21.3.c (ii) | C and D PPM | 1 | parameter
Voltage Theme | Reactive Power Capability below Maximum Capacity: P-Q/Pmax Profiles | 4.2.2.3.1 | Article 21.3.c.(i), (ii) and (iv): PPM: Parameters required for P-Q/Pmax Profiles | 32 | Qmax/Pmax (lag) (10kV, 20kV or 38kV Topology 3 & 4) | 0.65 p.u. | Power factor range from 0.92 [-0.42 Q / Pmax] to unity [0 Q/Pmax] | 21.3.c (ii) | C and D PPM | 1 | parameter
Voltage Theme | Reactive Power Capability below Maximum Capacity: P-Q/Pmax Profiles | 4.2.2.3.1 | Article 21.3.c.(i), (ii) and (iv): PPM: Parameters required for P-Q/Pmax Profiles | 33 | pmin (10kV, 20kV or 38kV Topology 5) | 0.0 p.u. | 0.12 p.u. | 21.3.c (ii) | C and D PPM | 1 | parameter
Voltage Theme | Reactive Power Capability below Maximum Capacity: P-Q/Pmax Profiles | 4.2.2.3.1 | Article 21.3.c.(i), (ii) and (iv): PPM: Parameters required for P-Q/Pmax Profiles | 33 | pmax (10kV, 20kV or 38kV Topology 5) | 1.0 p.u. | 1.0 p.u. | 21.3.c (ii) | C and D PPM | 1 | parameter
Voltage Theme | Reactive Power Capability below Maximum Capacity: P-Q/Pmax Profiles | 4.2.2.3.1 | Article 21.3.c.(i), (ii) and (iv): PPM: Parameters required for P-Q/Pmax Profiles | 33 | Qmin/Pmax (lead) (10kV, 20kV or 38kV Topology 5) | -0.5 p.u. | Power factor range from 0.92 [-0.42 Q / Pmax] to 0.95 [-0.33 Q/Pmax] | 21.3.c (ii) | C and D PPM | 1 | parameter
Voltage Theme | Reactive Power Capability below Maximum Capacity: P-Q/Pmax Profiles | 4.2.2.3.1 | Article 21.3.c.(i), (ii) and (iv): PPM: Parameters required for P-Q/Pmax Profiles | 33 | Qmax/Pmax (lag) (10kV, 20kV or 38kV Topology 5) | 0.65 p.u. | Power factor range from 0.92 [-0.42 Q / Pmax] to 0.95 [-0.33 Q/Pmax] | 21.3.c (ii) | C and D PPM | 1 | parameter
Voltage Theme | Reactive Power Capability below Maximum Capacity: P-Q/Pmax Profiles | 4.2.2.3.2 | Article 21.3.c.(iv): PPM: Time to Achieve Target Value within P-Q/Pmax Profile | 34 | Time to achieve target value [transmission connected] | Not specified | Without delay but within 20 seconds | 21.3.c.(iv) | C and D PPMs | 1 | parameter
Voltage Theme | Reactive Power Capability below Maximum Capacity: P-Q/Pmax Profiles | 4.2.2.3.2 | Article 21.3.c.(iv): PPM: Time to Achieve Target Value within P-Q/Pmax Profile | 34 | Time to achieve target value [distribution connected] | Not specified | Without delay but within 20 seconds | 21.3.c.(iv) | C and D PPMs | 1 | parameter
Voltage Theme | Supplementary Reactive Power Requirements | 4.2.2.4.1 | Article 18.2.a: SPGM: Supplementary reactive power requirements | 35 | Right to specify supplementary reactive power requirements when the connection point is remote | To specify or not to specify | RSOs reserve the right to specify | 18.2.a | Type C and D SPGMs | 1 | requirement
Voltage Theme | Supplementary Reactive Power Requirements | 4.2.2.4.2 | Article 21.3.a: PPM: Supplementary reactive power requirements | 36 | Right to specify supplementary reactive power requirements when the connection point is remote | To specify or not to specify | RSOs reserve the right to specify | 21.3.a | Type C and D PPMs | 1 | requirement
Voltage Theme | Reactive Power Control Modes for PPMs | 4.2.3.1 | Article 21.3.d.(iv)- Voltage Control Mode | 37 | t1 = time within which 90% of the change in reactive power is reached | 1 – 5 sec | 1 | 21.3.d.(iv) | C and D PGMs | 1 | parameter
Voltage Theme | Reactive Power Control Modes for PPMs | 4.2.3.1 | Article 21.3.d.(iv)- Voltage Control Mode | 37 | t2 = time within which 100% of the change in reactive power is reached | 5 – 60 sec | 5 | 21.3.d.(iv) | C and D PGMs | 3 | parameter
Voltage Theme | Reactive Power Control Modes for PPMs | 4.2.3.2 | Article 21.3.d (vi) - Power Factor Control Mode | 38 | Target power factor | Not specified | site-specific | 21.3.d.(vi) | C and D PGMs | 3 | parameter
Voltage Theme | Reactive Power Control Modes for PPMs | 4.2.3.2 | Article 21.3.d (vi) - Power Factor Control Mode | 38 | Time period to reach the set point | Not specified | site-specific | 21.3.d.(vi) | C and D PGMs | 3 | parameter
Voltage Theme | Reactive Power Control Modes for PPMs | 4.2.3.2 | Article 21.3.d (vi) - Power Factor Control Mode | 38 | Tolerance | Not specified | site-specific | 21.3.d.(vi) | C and D PGMs | 3 | parameter
Voltage Theme | Voltage Control System for SPGM | 4.2.4.1 | Article 19.2.a and 19.2.b.(v) | 39 | Power Threshold | Not specified | All Type D PGMs | 19.2.b.(v) | D SPGMs | 2 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.1 | Article 14.3.a & 16.3.a: FRT Capability for PGMs connected at voltage level <110 kV | 40 | Uret | 0.05-0.3 | 0.05 p.u. | 14.3.a & 16.3.a | B, C, D SPGMs | 3 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.1 | Article 14.3.a & 16.3.a: FRT Capability for PGMs connected at voltage level <110 kV | 40 | Uclear | 0.7-0.9 | 0.7 p.u. | 14.3.a & 16.3.a | B, C, D SPGMs | 3 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.1 | Article 14.3.a & 16.3.a: FRT Capability for PGMs connected at voltage level <110 kV | 40 | Urec1 | Uclear | Uclear | 14.3.a & 16.3.a | B, C, D SPGMs | 3 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.1 | Article 14.3.a & 16.3.a: FRT Capability for PGMs connected at voltage level <110 kV | 40 | Urec2 | 0.85-0.9 & >=Uclear | 0.9 p.u. | 14.3.a & 16.3.a | B, C, D SPGMs | 3 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.1 | Article 14.3.a & 16.3.a: FRT Capability for PGMs connected at voltage level <110 kV | 40 | tclear | 0.14-0.25 | 150 ms | 14.3.a & 16.3.a | B, C, D SPGMs | 3 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.1 | Article 14.3.a & 16.3.a: FRT Capability for PGMs connected at voltage level <110 kV | 40 | trec1 | tclear | tclear | 14.3.a & 16.3.a | B, C, D SPGMs | 3 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.1 | Article 14.3.a & 16.3.a: FRT Capability for PGMs connected at voltage level <110 kV | 40 | trec2 | trec1-0.7 | 450 ms | 14.3.a & 16.3.a | B, C, D SPGMs | 3 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.1 | Article 14.3.a & 16.3.a: FRT Capability for PGMs connected at voltage level <110 kV | 40 | trec3 | trec2-1.5 | trec2 | 14.3.a & 16.3.a | B, C, D SPGMs | 3 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.1 | Article 14.3.a & 16.3.a: FRT Capability for PGMs connected at voltage level <110 kV | 41 | Uret | 0.05-0.15 | 0.15 p.u. | 14.3.a & 16.3.a | B, C, D PPMs & offshore PPMs | 3 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.1 | Article 14.3.a & 16.3.a: FRT Capability for PGMs connected at voltage level <110 kV | 41 | Uclear | Uret -0.15 | Uret | 14.3.a & 16.3.a | B, C, D PPMs & offshore PPMs | 3 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.1 | Article 14.3.a & 16.3.a: FRT Capability for PGMs connected at voltage level <110 kV | 41 | Urec1 | Uclear | Uclear | 14.3.a & 16.3.a | B, C, D PPMs & offshore PPMs | 3 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.1 | Article 14.3.a & 16.3.a: FRT Capability for PGMs connected at voltage level <110 kV | 41 | Urec2 | 0.85 | 0.85 p.u. | 14.3.a & 16.3.a | B, C, D PPMs & offshore PPMs | 3 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.1 | Article 14.3.a & 16.3.a: FRT Capability for PGMs connected at voltage level <110 kV | 41 | tclear | 0.14-0.25 | 250 ms | 14.3.a & 16.3.a | B, C, D PPMs & offshore PPMs | 3 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.1 | Article 14.3.a & 16.3.a: FRT Capability for PGMs connected at voltage level <110 kV | 41 | trec1 | tclear | tclear | 14.3.a & 16.3.a | B, C, D PPMs & offshore PPMs | 3 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.1 | Article 14.3.a & 16.3.a: FRT Capability for PGMs connected at voltage level <110 kV | 41 | trec2 | trec1 | trec1 | 14.3.a & 16.3.a | B, C, D PPMs & offshore PPMs | 3 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.1 | Article 14.3.a & 16.3.a: FRT Capability for PGMs connected at voltage level <110 kV | 41 | trec3 | 1.5-3.0 | 2.9 s | 14.3.a & 16.3.a | B, C, D PPMs & offshore PPMs | 3 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.2 | Article 16.3.a FRT Capability for PGMs connected at voltage level ³110 kV | 42 | Uret | 0 | 0 | 16.3.a | D SPGMs | 3 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.2 | Article 16.3.a FRT Capability for PGMs connected at voltage level ³110 kV | 42 | Uclear | 0.25 | 0.25 p.u. | 16.3.a | D SPGMs | 3 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.2 | Article 16.3.a FRT Capability for PGMs connected at voltage level ³110 kV | 42 | Urec1 | 0.5-0.7 | 0.5 p.u. | 16.3.a | D SPGMs | 3 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.2 | Article 16.3.a FRT Capability for PGMs connected at voltage level ³110 kV | 42 | Urec2 | 0.85-0.9 | 0.9 p.u. | 16.3.a | D SPGMs | 3 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.2 | Article 16.3.a FRT Capability for PGMs connected at voltage level ³110 kV | 42 | tclear | 0.14-0.25 | 150 ms | 16.3.a | D SPGMs | 3 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.2 | Article 16.3.a FRT Capability for PGMs connected at voltage level ³110 kV | 42 | trec1 | tclear -0.45 | 450 ms | 16.3.a | D SPGMs | 3 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.2 | Article 16.3.a FRT Capability for PGMs connected at voltage level ³110 kV | 42 | trec2 | trec1-0.7 | 450 ms | 16.3.a | D SPGMs | 3 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.2 | Article 16.3.a FRT Capability for PGMs connected at voltage level ³110 kV | 42 | trec3 | trec2-1.5 | 450 ms | 16.3.a | D SPGMs | 3 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.2 | Article 16.3.a FRT Capability for PGMs connected at voltage level ³110 kV | 43 | Uret | 0 | 0 | 16.3.a | D PPMs & offshore PPMs | 1 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.2 | Article 16.3.a FRT Capability for PGMs connected at voltage level ³110 kV | 43 | Uclear | Uret | Uret | 16.3.a | D PPMs & offshore PPMs | 1 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.2 | Article 16.3.a FRT Capability for PGMs connected at voltage level ³110 kV | 43 | Urec1 | Uclear | Uclear | 16.3.a | D PPMs & offshore PPMs | 1 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.2 | Article 16.3.a FRT Capability for PGMs connected at voltage level ³110 kV | 43 | Urec2 | 0.85 | 0.85 p.u. | 16.3.a | D PPMs & offshore PPMs | 1 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.2 | Article 16.3.a FRT Capability for PGMs connected at voltage level ³110 kV | 43 | tclear | 0.14-0.25 | 150 ms | 16.3.a | D PPMs & offshore PPMs | 1 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.2 | Article 16.3.a FRT Capability for PGMs connected at voltage level ³110 kV | 43 | trec1 | tclear | tclear | 16.3.a | D PPMs & offshore PPMs | 1 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.2 | Article 16.3.a FRT Capability for PGMs connected at voltage level ³110 kV | 43 | trec2 | trec1 | trec1 | 16.3.a | D PPMs & offshore PPMs | 1 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.2 | Article 16.3.a FRT Capability for PGMs connected at voltage level ³110 kV | 43 | trec3 | 1.5-3.0 | 2.9 s | 16.3.a | D PPMs & offshore PPMs | 1 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.3.1 | Article 20.2.b Fast Fault Current Injection for Symmetrical Faults | 44 | Voltage threshold for fast fault current injection | Not specified | During voltage dips i.e. when the voltage is below 0.9 p.u. | 20.2.b | B, C and D PPMs | 1 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.3.1 | Article 20.2.b Fast Fault Current Injection for Symmetrical Faults | 44 | End of the voltage deviation | Not specified | Once the voltage has recovered to within normal operating voltage range | 20.2.b | B, C and D PPMs | 1 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.3.1 | Article 20.2.b Fast Fault Current Injection for Symmetrical Faults | 44 | the characteristics of the fast fault current, including the time domain for measuring the voltage deviation and fast fault current | Not specified | Reactive current should be provided for the duration of the voltage deviation within the rating of the PPM | 20.2.b | B, C and D PPMs | 1 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.3.1 | Article 20.2.b Fast Fault Current Injection for Symmetrical Faults | 44 | the timing and accuracy of the fast fault current, which may include several stages during a fault and after its clearance | Not specified | Rise Time no greater than 100ms and a Settling Time no greater than 300ms. | 20.2.b | B, C and D PPMs | 2 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.3.2 | Article 20.2.c Fast Fault Current Injection for Asymmetrical Faults | 45 | Voltage threshold for fast fault current injection | Not specified | During voltage dips i.e. when the voltage is below 0.9 p.u. | 20.2.b | B, C and D PPMs | 1 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.3.2 | Article 20.2.c Fast Fault Current Injection for Asymmetrical Faults | 45 | the characteristics of the fast fault current, including the time domain for measuring the voltage deviation and fast fault current | Not specified | Reactive current should be provided for the duration of the voltage deviation within the rating of the PPM | 20.2.b | B, C and D PPMs | 1 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.3.2 | Article 20.2.c Fast Fault Current Injection for Asymmetrical Faults | 45 | the timing and accuracy of the fast fault current, which may include several stages during a fault and after its clearance | Not specified | Rise Time no greater than 100ms and a Settling Time no greater than 300ms. | 20.2.b | B, C and D PPMs | 2 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.4 | Article 20.3.a Post-Fault Active Power Recovery for PPMs | 46 | when the post-fault active power recovery begins, based on a voltage criterion | Not specified | un< 0.9 p.u. | 20.3.a | B, C and D PPMs & offshore PPMs | 1 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.4 | Article 20.3.a Post-Fault Active Power Recovery for PPMs | 46 | maximum allowed time for active power recovery | Not specified | 500ms/1s | 20.3.a | B, C and D PPMs & offshore PPMs | 1 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.4 | Article 20.3.a Post-Fault Active Power Recovery for PPMs | 46 | magnitude and accuracy for active power recovery | Not specified | 90% | 20.3.a | B, C and D PPMs & offshore PPMs | 1 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.5 | Article 21.3.e Priority Given to Active or Reactive Power Contribution for PPMs | 47 | Prioritisation requirements during FRT | Active/Reactive | Active | 21.3.e | C and D PPMs | 3 | parameter
Voltage Theme | Non-Mandatory Voltage Theme Requirements that we are not invoking at this time | 4.2.6 | Non-Mandatory Voltage Theme Requirements that we are not invoking at this time | 48 | Simultaneous overvoltage and underfrequency or simultaneous undervoltage and overfrequency | Do we want to expertise the right to specify this non-mandatory RfG? | Not invoking | 16(02)(a)(ii) | Type A, B, C and D PGMs |  | requirement
System Restoration Theme | Operation following Tripping to House Load | 4.3.1 | Article 15.5.c.(iii) Operation following tripping to house load | 49 | Operation Following Tripping to House Load | Not Specified | 4 hours | 15.5.c.iii | C and D PGMs with a minimum re-synchronisation time greater than 15 minutes* | 3 | parameter
Protection and Instrumentation Theme | Manual, local measures where the automatic remote devices are out of service | 4.4.1 | Article 15.2.b: Manual, local measures where the automatic remote devices are out of service | 50 | Time required to achieve setpoint when automatic remote devices are unavailable | Not Specified | 1 hour | 15(2)(b) | B, C and D PGMs | 3 | parameter
Protection and Instrumentation Theme | Instrumentation: Quality of Supplies | 4.4.2 | Article 15.6.b (i): Instrumentation: Quality of Supplies | 51 | Quality of supplies parameters to be recorded. | Not Specified | Site Specific | 15(6)(b)(i) | C and D PGMs & offshore PPMs | 1 | requirement
Protection and Instrumentation Theme | Dynamic System Behaviour Monitoring | 4.4.3 | Article 15.6.b.(iii): Dynamic System Behaviour Monitoring | 52 | oscillation trigger detecting poorly damped power oscillations. | Not Specified | Site Specific | 15(6)(b)(iii) | C and D PGMs & offshore PPMs | 1 | parameter
Protection and Instrumentation Theme | Simulation Model Provision | 4.4.4 | Article 15.6.c.(iii) Simulation Model Provision | 53 | Model Provision | Not Specified | Retain the existing model provision requirements with the inclusion of min and max short circuit levels as part of Grid Code Planning Code Appendix Generator Data Requirements | 15(6)(c)(iii) | C and D PGMs & offshore PPMs | 2 | requirement
Protection and Instrumentation Theme | Neutral-point at the network side of step transformers | 4.4.5 | Article 15.6.f.: Neutral-point at the network side of step transformers | 54 | Earthing arrangement of the neutral-point | Not Specified | 400 kV – solidly earthed 220 kV – site specific 110 kV – site specific | 15(6)(f) | C and D PGMs & offshore PPMs | 1 | parameter
Protection and Instrumentation Theme | Non-Mandatory Protection Theme Requirements that are not for consultation but will be agreed on a case by case basis | 4.4.6 | Non-Mandatory Protection Theme Requirements that are not for consultation but will be agreed on a case by case basis | 55 | Control Scheme and Settings: Agreement and coordination between the TSO, the RSO (TSO and DSO) and the power generating facility owner (PGFO) | Control schemes and settings of the control devices | Case by case basis | 14.5.a | B,C,D PGMs & offshore PPMs | N/A | parameter
Protection and Instrumentation Theme | Non-Mandatory Protection Theme Requirements that are not for consultation but will be agreed on a case by case basis | 4.4.6 | Non-Mandatory Protection Theme Requirements that are not for consultation but will be agreed on a case by case basis | 55 | Electrical Protection Schemes and settings: Agreement and coordination between the RSO and the PGFO | Protection schemes and settings | Case by case basis | 14.5.b | B,C,D PGMs & offshore PPMs | N/A | parameter
Protection and Instrumentation Theme | Non-Mandatory Protection Theme Requirements that are not for consultation but will be agreed on a case by case basis | 4.4.6 | Non-Mandatory Protection Theme Requirements that are not for consultation but will be agreed on a case by case basis | 55 | Loss of angular stability or loss of control: Agreement between PGFO and the RSO (DSO or TSO), in coordination with the TSO | Criteria to detect loss of angular stability or loss of control | Case by case basis | 15.6.a | C.D PGM & Offshore PPMs | N/A | parameter
Protection and Instrumentation Theme | Non-Mandatory Protection Theme Requirements that are not for consultation but will be agreed on a case by case basis | 4.4.6 | Non-Mandatory Protection Theme Requirements that are not for consultation but will be agreed on a case by case basis | 55 | Instrumentation: Settings of the fault recording equipment, including triggering criteria and sampling rate | Settings of the fault recording equipment, including triggering criteria and sampling rate | Case by case basis | 15.6.b(ii) | C.D PGM & Offshore PPMs | N/A | parameter
Protection and Instrumentation Theme | Non-Mandatory Protection Theme Requirements that are not for consultation but will be agreed on a case by case basis | 4.4.6 | Non-Mandatory Protection Theme Requirements that are not for consultation but will be agreed on a case by case basis | 55 | Agreement between the PGFO and the RSO (DSO or TSO), in coordination with the TSO. |  | Case by case basis | 15.6.b(ii) | C.D PGM & Offshore PPMs | N/A | parameter
Protection and Instrumentation Theme | Non-Mandatory Protection Theme Requirements that are not for consultation but will be agreed on a case by case basis | 4.4.6 | Non-Mandatory Protection Theme Requirements that are not for consultation but will be agreed on a case by case basis | 55 | Instrumentation: Protocols for recorded data | Protocols for recorded data | Case by case basis | 15.6.b(iv) | C.D PGM & Offshore PPMs | N/A | parameter
Protection and Instrumentation Theme | Non-Mandatory Protection Theme Requirements that are not for consultation but will be agreed on a case by case basis | 4.4.6 | Non-Mandatory Protection Theme Requirements that are not for consultation but will be agreed on a case by case basis | 55 | Agreement between PGFO, the RSO and the relevant TSO |  | Case by case basis | 15.6.b(iv) | C.D PGM & Offshore PPMs | N/A | parameter
Protection and Instrumentation Theme | Non-Mandatory Protection Theme Requirements that are not for consultation but will be agreed on a case by case basis | 4.4.6 | Non-Mandatory Protection Theme Requirements that are not for consultation but will be agreed on a case by case basis | 55 | Installation of devices for system operations and system security: Agreement between RSO or TSO and PGFO | Definition of the devices needed for system operation and system security | Case by case basis | 15.6.d | C.D PGM & Offshore PPMs | N/A | parameter
Protection and Instrumentation Theme | Non-Mandatory Protection Theme Requirements that are not for consultation but will be agreed on a case by case basis | 4.4.6 | Non-Mandatory Protection Theme Requirements that are not for consultation but will be agreed on a case by case basis | 55 | Synchronisation: Agreement between the RSO and the PGFO | Settings of the synchronisation devices | Case by case basis | 16.4 | D PGM & offshore PPMs | N/A | parameter
Protection and Instrumentation Theme | Non-Mandatory Protection Theme Requirements that are not for consultation but will be agreed on a case by case basis | 4.4.6 | Non-Mandatory Protection Theme Requirements that are not for consultation but will be agreed on a case by case basis | 55 | Angular stability under fault conditions: Agreement between the TSO and PGFO | Agreement for technical capabilities of the power generating module to aid angular stability. | Case by case basis | 19.3 | D SPGM | N/A | parameter
Note on G145: Ryan, Miriam: Should this be "trec2 - 900 ms"?