## Northern Ireland
Theme | Sub-Theme | Document Heading Number | Article / Heading | Table Number | Parameter | Parameter in RfG | Consultation Proposal | Article Number | Type Applicability | Justification Code | Parameter or Requirement | Comment
Frequency Theme | Frequency ranges | 4.1.1.1 | Article 13.1 (a) (i): Frequency Ranges | 1 | Frequency Ranges | 48,5 Hz-49,0 Hz for a time to be specified by each TSO, but not less than 90 minutes | 90 Minutes | 13.1.a.(i) | A, B, C, D PGMs and Offshore PPMs | 2 | parameter
Frequency Theme | Rate of Change of Frequency | 4.1.2.1 | Article 13.1 (b): RoCoF | 2 | The maximum RoCoF for which the Power Generating Module (PGM) shall stay connected | Not Specified | 1 Hz/s over 500ms window | 13.1.b | A, B, C and D PGMs and Offshore PPMs | 1 | parameter
Frequency Theme | Rate of Change of Frequency | 4.1.2.1 | Article 13.1 (b): RoCoF | 2 | The proposal for loss of mains protection | Not Specified | is 1 Hz/Sec with a 500ms delay. | 13.1.b | A, B, C and D and Offshore PPMs | 1 | parameter
Frequency Theme | Active Power Control | 4.1.3.1 | Article 13.4.a: Admissible reduction from maximum output with falling frequency | 3 | Admissible active power reduction from maximum output with falling frequency | below 49 Hz falling by a reduction rate of 2% of the maximum capacity at 50 Hz per 1 Hz frequency drop or below 49.5 Hz falling by a reduction rate of 10% of the maximum capacity at 50 Hz per 1 Hz frequency drop. | below 49 Hz falling by a reduction rate of 2% of the maximum capacity at 50 Hz per 1 Hz frequency drop | 13.4 (a) | A, B, C and D PGMs | 3 | parameter
Frequency Theme | Active Power Control | 4.1.3.2 | Article 13.5: Admissible reduction from maximum output with falling frequency taking Account of Technical Capabilities of PGMs | 4 | Ambient Conditions | Not Specified | 10°C, 70% relative humidity and 1013 hPa for gas fired turbine generators | 13.5 | Gas-fired SPGMs (A, B, C and D). | 3 | parameter
Frequency Theme | Active Power Control | 4.1.3.3 | Article 13.6: Remote operation of facility to cease active power output | 5 | Specify requirements for equipment to make this facility operable remotely for Type A | A right to specify | Maintain the right to specify for Type A only in due time for plant design (c/f Art 14 (2) (b) for Type B | 13.6 | A PGMs | 3 | requirement
Frequency Theme | Active Power Control | 4.1.3.4 | Article 13.7: Automatic connection to the network | 6 | (i) Frequency Ranges and Time Delay | Non-specific | 47 Hz to 50.1 Hz with a five minute delay | 13.7 | A, B, and C PGMs | 1 | parameter
Frequency Theme | Active Power Control | 4.1.3.4 | Article 13.7: Automatic connection to the network | 6 | (ii) Maximum admissible gradient of increase in power | Non-specific | 10% of Pmax per minute | 13.7 | A, B and C PGMs | 1 | parameter
Frequency Theme | Active Power Control | 4.1.3.4 | Article 13.7: Automatic connection to the network | 6 | (iii) Allowing automatic connection | A right to not allow | Allow automatic connection for Type A & B Do not allow automatic connection for Type C | 13.7 | A, B and C PGMs | 1 | parameter
Frequency Theme | Active Power Control | 4.1.3.5 | Article 14.2.b: Remote operation of power output | 7 | Right to specify the requirements for further equipment to allow active power output to be remotely operated | To specify or not to specify | RSO to specify for Type B generators; in due time for plant design. | 14.2 (b) | B PGMs | 3 | requirement
Frequency Theme | Active Power Control | 4.1.3.6 | Article 15.2.a: Achieving Active Power Set points | 8 | The period within which the adjusted active power setpoint must be reached | No range provided | PPM controllable generation The Active power set point and the time to achieve this is determined by the TSO , however following shut down a PPM must commence active power export within 90secs WFPS setting schedule 6.11 SPGM dispatchable generation Active power set point and time to achieve the set point is given via TSO dispatch instructions in accordance with SDC2. Minimum ramp rates and start-up times specified in CC.S1.3.7 & CC.S1.2.3.4 | 15.2 (a) | C and D PGMs | 1 | parameter
Frequency Theme | Active Power Control | 4.1.3.6 | Article 15.2.a: Achieving Active Power Set points | 8 | Tolerance (subject to the availability of the prime mover resource) applying to the new setpoint and the time within which it must be reached | No Range Provided | PPM controllable generation. Active power output to be within 3% of set point (based on RC) Time to achieve set point within ±10 seconds of target time. (See WFPS Setting Schedule 6.1) SPGM dispatchable generation Tolerance bands for dispatch instructions is specified in OC11 Part B | 15.2 (a) | C and D PGMs | 3 | parameter
Frequency Theme | Frequency Modes | 4.1.4.2 | Article 13.2.a: LFSM-O Parameter Selection | 9 | Frequency threshold | Between 50.2- 50.5 Hz | 50.2 Hz | 13.2(a) | A, B, C and D PGMs & offshore PPMs | 2 | parameter
Frequency Theme | Frequency Modes | 4.1.4.2 | Article 13.2.a: LFSM-O Parameter Selection | 9 | Droop settings | Between 2-12 % | Machines should be capable of operating in the range 2-12%. The default setting is 4% | 13.2(a) | A, B, C and D PGMs & offshore PPMs | 2 | parameter
Frequency Theme | Frequency Modes | 4.1.4.3 | Article 13.2.b: LFSM-O: Automatic disconnection and reconnection | 10 | Automatic disconnection and reconnection of PGMs | Allow or do not allow | Do not allow | 13.2 (b) | A PGMs | 3 | requirement
Frequency Theme | Frequency Modes | 4.1.4.4 | Article 13.2.f: LFSM-O: Actions at minimum regulating level | 11 | Actions in LFSM-O upon reaching minimum regulating level, | Choose between (i) continuing operation at this level; or (ii) further decreasing active power output | (ii) further decreasing active power output | 13.2 (f) | A, B, C and D PGMs & offshore PPMs | 1 | requirement
Frequency Theme | Frequency Modes | 4.1.4.5 | Article 15.2.c: LFSM-U Parameter Selection | 12 | Frequency threshold | between 49.8 Hz and 49.5 Hz inclusive | 49.5 Hz | 15.2 (c) | C and D PGMs & offshore PPMs | 1 | parameter
Frequency Theme | Frequency Modes | 4.1.4.5 | Article 15.2.c: LFSM-U Parameter Selection | 12 | Droop settings | 2-12% | Default is 4% unless otherwise specified by the TSO on a site specific basis | 15.2 (c) | C and D PGMs & offshore PPMs | 1 | parameter
Frequency Theme | Frequency Modes | 4.1.4.6 | Article 15.2.d.(i) and (ii): FSM Parameter Selection | 13 | Active Power Range (ΔP/Pmax) | 1.5-10% | Not proposing a value at this time | 15.2 (d) (i) and (ii) | C and D PGMs & offshore PPMs | 1 | parameter
Frequency Theme | Frequency Modes | 4.1.4.6 | Article 15.2.d.(i) and (ii): FSM Parameter Selection | 13 | Frequency Response Insensitivity (Δf) | 10-30 mHz | 15mHz* | 15.2 (d) (i) and (ii) | C and D PGMs & offshore PPMs | 3 | parameter
Frequency Theme | Frequency Modes | 4.1.4.6 | Article 15.2.d.(i) and (ii): FSM Parameter Selection | 13 | Frequency Response Insensitivity (Δf/f) | 0.02-0.06% | 0.03% | 15.2 (d) (i) and (ii) | C and D PGMs & offshore PPMs | 3 | parameter
Frequency Theme | Frequency Modes | 4.1.4.6 | Article 15.2.d.(i) and (ii): FSM Parameter Selection | 13 | Frequency Response Deadband | 0-500mHz | +/-15mHz* | 15.2 (d) (i) and (ii) | C and D PGMs& offshore PPMs | 3 | parameter
Frequency Theme | Frequency Modes | 4.1.4.6 | Article 15.2.d.(i) and (ii): FSM Parameter Selection | 13 | Droop | 2-12% | Depends on gen type – default is 4% | 15.2 (d) (i) and (ii) | C and D PGMs & offshore PPMs | 1 | parameter
Frequency Theme | Frequency Modes | 4.1.4.7 | Article 15.2.d.(iii): FSM: Step Change in Frequency | 14 | Active power range | 1.5-10% | 10% | 15.2 (d) (iii) | C and D PGMs & offshore PPMs | 3 | parameter
Frequency Theme | Frequency Modes | 4.1.4.7 | Article 15.2.d.(iii): FSM: Step Change in Frequency | 14 | Admissible initial time delay for activation of active power frequency response for PPMs | Less than 2 seconds | 0s No time delays other than those inherent in the design of the frequency response system | 15.2 (d) (iii) | C and D PGMs & offshore PPMs | 3 | parameter
Frequency Theme | Frequency Modes | 4.1.4.7 | Article 15.2.d.(iii): FSM: Step Change in Frequency | 14 | Maximum admissible choice of full activation time | 30 seconds | 15 seconds | 15.2 (d) (iii) | C and D PGMs & offshore PPMs | 3 | parameter
Frequency Theme | Frequency Modes | 4.1.4.7 | Article 15.2.d.(iii): FSM: Step Change in Frequency | 14 | Capability relating to the duration of provision of full active power frequency response | 15-30 minutes | 20 | 15.2 (d) (v) | C and D PGMs & offshore PPMs | 3 | parameter
Frequency Theme | Non-Mandatory Frequency Requirements that we are not invoking at this time | 4.1.5 | Non-Mandatory Frequency Requirements that we are not invoking at this time | 15 | Shorter initial FSM response delay for PGMs without inertia | Not specified | Not Mandatory – can be agreed on a case by case basis with System Services Contracts | 15.2.d(iv) | Type A, B, C and D PGMs and offshore PPMs | N/A | requirement
Frequency Theme | Non-Mandatory Frequency Requirements that we are not invoking at this time | 4.1.5 | Non-Mandatory Frequency Requirements that we are not invoking at this time | 15 | Synthetic inertia capability for PPM | Not Specified | Not Mandatory – can be agreed on a case by case basis with System Services Contracts | 21(2) | C and D PPMs | N/A | requirement
Voltage Theme | Automatic Disconnection Due to Voltage Level | 4.2.1.1 | Article 15.3: Type C Automatic Disconnection Due to Voltage Level | 16 | Minimum Voltage below which Module will automatic disconnect | Not specified | Specificed at plant design stage | 15.3 | C (PPM) | 1 | parameter
Voltage Theme | Automatic Disconnection Due to Voltage Level | 4.2.1.1 | Article 15.3: Type C Automatic Disconnection Due to Voltage Level | 16 | Maximum Voltage above which Module will automatic disconnect | Not specified | Specificed at plant design stage | 15.3 | C PGMs | 1 | parameter
Voltage Theme | Automatic Disconnection Due to Voltage Level | 4.2.1.2 | Article 16.2.c: Type D Automatic Disconnection Due to Voltage Level | 17 | Minimum Voltage below which Module will automatic disconnect | Not specified | Not Allowed | 16.2.c | D PGMs | 3 | parameter
Voltage Theme | Automatic Disconnection Due to Voltage Level | 4.2.1.2 | Article 16.2.c: Type D Automatic Disconnection Due to Voltage Level | 17 | Maximum Voltage above which Module will automatic disconnect | Not specified | Not Allowed | 16.2.c | D PGMs | 3 | parameter
Voltage Theme | Reactive Power Capability for Type B PGMs | 4.2.2.1.1 | Article 17.2.a: Reactive Power capability for Type B SPGMs | 18 | umin (Low Voltage ) | 0.875 pu | 0.94 pu | 17.2 (a) and 20.2 (a) | B | 1 | parameter
Voltage Theme | Reactive Power Capability for Type B PGMs | 4.2.2.1.1 | Article 17.2.a: Reactive Power capability for Type B SPGMs | 18 | umax (Low Voltage ) | 1.1 pu | 1.1 pu | 17.2 (a) and 20.2 (a) | B | 1 | parameter
Voltage Theme | Reactive Power Capability for Type B PGMs | 4.2.2.1.1 | Article 17.2.a: Reactive Power capability for Type B SPGMs | 18 | Qmin/Pmax (lead) (Low Voltage ) | -0.5 pu | -0.33 pu | 17.2 (a) and 20.2 (a) | B | 1 | parameter
Voltage Theme | Reactive Power Capability for Type B PGMs | 4.2.2.1.1 | Article 17.2.a: Reactive Power capability for Type B SPGMs | 18 | Qmax/Pmax (lag) (Low Voltage ) | 0.65 pu | 0.203 pu | 17.2 (a) and 20.2 (a) | B | 1 | parameter
Voltage Theme | Reactive Power Capability for Type B PGMs | 4.2.2.1.1 | Article 17.2.a: Reactive Power capability for Type B SPGMs | 18 | umin (Below 110kV ) | 0.875 pu | 0.94 pu | 17.2 (a) and 20.2 (a) | B | 1 | parameter
Voltage Theme | Reactive Power Capability for Type B PGMs | 4.2.2.1.1 | Article 17.2.a: Reactive Power capability for Type B SPGMs | 18 | umax (Below 110kV ) | 1.1 pu | 1.06 pu | 17.2 (a) and 20.2 (a) | B | 1 | parameter
Voltage Theme | Reactive Power Capability for Type B PGMs | 4.2.2.1.1 | Article 17.2.a: Reactive Power capability for Type B SPGMs | 18 | Qmin/Pmax (lead) (Below 110kV ) | -0.5 pu | -0.33 pu | 17.2 (a) and 20.2 (a) | B | 1 | parameter
Voltage Theme | Reactive Power Capability for Type B PGMs | 4.2.2.1.1 | Article 17.2.a: Reactive Power capability for Type B SPGMs | 18 | Qmax/Pmax (lag) (Below 110kV ) | 0.65 pu | 0.203 pu | 17.2 (a) and 20.2 (a) | B | 1 | parameter
Voltage Theme | Reactive Power Capability for Type B PGMs | 4.2.2.1.2 | Article 20.2.a: Reactive Power capability for Type B PPMs | 19 | umin (Low Voltage ) | 0.875 pu | 0.94 pu | 17.2 (a) and 20.2 (a) | B | 1 | parameter
Voltage Theme | Reactive Power Capability for Type B PGMs | 4.2.2.1.2 | Article 20.2.a: Reactive Power capability for Type B PPMs | 19 | umax (Low Voltage ) | 1.1 pu | 1.1 pu | 17.2 (a) and 20.2 (a) | B | 1 | parameter
Voltage Theme | Reactive Power Capability for Type B PGMs | 4.2.2.1.2 | Article 20.2.a: Reactive Power capability for Type B PPMs | 19 | Qmin/Pmax (lead) (Low Voltage ) | -0.5 pu | -0.33 pu | 17.2 (a) and 20.2 (a) | B | 1 | parameter
Voltage Theme | Reactive Power Capability for Type B PGMs | 4.2.2.1.2 | Article 20.2.a: Reactive Power capability for Type B PPMs | 19 | Qmax/Pmax (lag) (Low Voltage ) | 0.65 pu | 0.203 pu | 17.2 (a) and 20.2 (a) | B | 1 | parameter
Voltage Theme | Reactive Power Capability for Type B PGMs | 4.2.2.1.2 | Article 20.2.a: Reactive Power capability for Type B PPMs | 19 | umin (Below 110kV ) | 0.875 pu | 0.94 pu | 17.2 (a) and 20.2 (a) | B | 1 | parameter
Voltage Theme | Reactive Power Capability for Type B PGMs | 4.2.2.1.2 | Article 20.2.a: Reactive Power capability for Type B PPMs | 19 | umax (Below 110kV ) | 1.1 pu | 1.06 pu | 17.2 (a) and 20.2 (a) | B | 1 | parameter
Voltage Theme | Reactive Power Capability for Type B PGMs | 4.2.2.1.2 | Article 20.2.a: Reactive Power capability for Type B PPMs | 19 | Qmin/Pmax (lead) (Below 110kV ) | -0.5 pu | -0.33 pu | 17.2 (a) and 20.2 (a) | B | 1 | parameter
Voltage Theme | Reactive Power Capability for Type B PGMs | 4.2.2.1.2 | Article 20.2.a: Reactive Power capability for Type B PPMs | 19 | Qmax/Pmax (lag) (Below 110kV ) | 0.65 pu | 0.203 pu | 17.2 (a) and 20.2 (a) | B | 1 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.1 | Article 18.2.b.(i): SPGM: Parameters required for U-Q/Pmax Profiles | 20 | umin (110 kV ) | 0.875 p.u. | 0.9 pu | 18.2.b (ii) | D SPGMs | 1 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.1 | Article 18.2.b.(i): SPGM: Parameters required for U-Q/Pmax Profiles | 20 | umax (110 kV ) | 1.1 p.u. | 1.1 pu | 18.2.b (ii) | D SPGMs | 1 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.1 | Article 18.2.b.(i): SPGM: Parameters required for U-Q/Pmax Profiles | 20 | Qmin/Pmax (lead) (110 kV ) | -0.5 p.u. | -0.48 pu | 18.2.b (ii) | D SPGMs | 3 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.1 | Article 18.2.b.(i): SPGM: Parameters required for U-Q/Pmax Profiles | 20 | Qmax/Pmax (lag) (110 kV ) | 0.65 p.u. | 0.6 pu | 18.2.b (ii) | D SPGMs | 3 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.1 | Article 18.2.b.(i): SPGM: Parameters required for U-Q/Pmax Profiles | 20 | umin (275 kV) | 0.875 p.u. | 0.9 pu | 18.2.b (ii) | D SPGMs | 1 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.1 | Article 18.2.b.(i): SPGM: Parameters required for U-Q/Pmax Profiles | 20 | umax (275 kV) | 1.1 p.u. | 1.1 pu | 18.2.b (ii) | D SPGMs | 1 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.1 | Article 18.2.b.(i): SPGM: Parameters required for U-Q/Pmax Profiles | 20 | Qmin/Pmax (lead) (275 kV) | -0.5 p.u. | -0.48 pu | 18.2.b (ii) | D SPGMs | 3 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.1 | Article 18.2.b.(i): SPGM: Parameters required for U-Q/Pmax Profiles | 20 | Qmax/Pmax (lag) (275 kV) | 0.65 p.u. | 0.6 pu | 18.2.b (ii) | D SPGMs | 3 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.1 | Article 18.2.b.(i): SPGM: Parameters required for U-Q/Pmax Profiles | 20 | umin (400 kV) | 0.875 p.u. | 0.875 pu | 18.2.b (ii) | D SPGMs | 3 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.1 | Article 18.2.b.(i): SPGM: Parameters required for U-Q/Pmax Profiles | 20 | umax (400 kV) | 1.1 p.u. | 1.05 pu | 18.2.b (ii) | D SPGMs | 3 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.1 | Article 18.2.b.(i): SPGM: Parameters required for U-Q/Pmax Profiles | 20 | Qmin/Pmax (lead) (400 kV) | -0.5 p.u. | -0.48pu | 18.2.b (ii) | D SPGMs | 3 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.1 | Article 18.2.b.(i): SPGM: Parameters required for U-Q/Pmax Profiles | 20 | Qmax/Pmax (lag) (400 kV) | 0.65 p.u. | 0.6 pu | 18.2.b (ii) | D SPGMs | 3 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.1 | Article 18.2.b.(i): SPGM: Parameters required for U-Q/Pmax Profiles | 21 | umin (Below 110kV ) | 0.875 p.u. | 0.94 pu | 18.2.b (ii) | C and D SPGMs | 1 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.1 | Article 18.2.b.(i): SPGM: Parameters required for U-Q/Pmax Profiles | 21 | umax (Below 110kV ) | 1.1 p.u. | 1.06 pu | 18.2.b (ii) | C and D SPGMs | 1 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.1 | Article 18.2.b.(i): SPGM: Parameters required for U-Q/Pmax Profiles | 21 | Qmin/Pmax (import) (Below 110kV ) | -0.5 p.u. | -0.33 pu | 18.2.b (ii) | C and D SPGMs | 1 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.1 | Article 18.2.b.(i): SPGM: Parameters required for U-Q/Pmax Profiles | 21 | Qmax/Pmax (Export) (Below 110kV ) | 0.65 p.u. | 0.33 pu | 18.2.b (ii) | C and D SPGMs | 1 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.2 | Article 18.2.b. (iv): SPGM: Time to Achieve Target Value within U-Q/Pmax Profile | 22 | Time to achieve target value | Not specified | Without undue delay but at least within 120 seconds | 18.2.b (iv) | C and D SPGMs | 3 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.3 | Article 21.3.b (i) and (ii) & Article 25.5: PPM: Parameters required for U-Q/Pmax Profiles | 23 | umin (110 kV) | 0.875 p.u. | 0.9 p.u. | 21.3.b (ii) | D PPMs | 1 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.3 | Article 21.3.b (i) and (ii) & Article 25.5: PPM: Parameters required for U-Q/Pmax Profiles | 23 | umax (110 kV) | 1.1 p.u. | 1.1 p.u. | 21.3.b (ii) | D PPMs | 1 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.3 | Article 21.3.b (i) and (ii) & Article 25.5: PPM: Parameters required for U-Q/Pmax Profiles | 23 | Qmin/Pmax (lead) (110 kV) | -0.5 p.u. | -0.33 p.u. | 21.3.b (ii) | D PPMs | 1 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.3 | Article 21.3.b (i) and (ii) & Article 25.5: PPM: Parameters required for U-Q/Pmax Profiles | 23 | Qmax/Pmax (lag) (110 kV) | 0.65 p.u. | 0.33 p.u. | 21.3.b (ii) | D PPMs | 1 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.3 | Article 21.3.b (i) and (ii) & Article 25.5: PPM: Parameters required for U-Q/Pmax Profiles | 23 | umin (275 kV) | 0.875 p.u. | 0.9 p.u. | 21.3.b (ii) | D PPMs | 1 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.3 | Article 21.3.b (i) and (ii) & Article 25.5: PPM: Parameters required for U-Q/Pmax Profiles | 23 | umax (275 kV) | 1.1 p.u. | 1.1 p.u. | 21.3.b (ii) | D PPMs | 1 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.3 | Article 21.3.b (i) and (ii) & Article 25.5: PPM: Parameters required for U-Q/Pmax Profiles | 23 | Qmin/Pmax (lead) (275 kV) | -0.5 p.u. | -0.33 p.u. | 21.3.b (ii) | D PPMs | 1 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.3 | Article 21.3.b (i) and (ii) & Article 25.5: PPM: Parameters required for U-Q/Pmax Profiles | 23 | Qmax/Pmax (lead) (275 kV) | 0.65 p.u. | 0.33 p.u. | 21.3.b (ii) | D PPMs | 1 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.3 | Article 21.3.b (i) and (ii) & Article 25.5: PPM: Parameters required for U-Q/Pmax Profiles | 23 | umin (400 kV) | 0.875 p.u. | 0.875 p.u. | 21.3.b (ii) | D PPMs | 3 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.3 | Article 21.3.b (i) and (ii) & Article 25.5: PPM: Parameters required for U-Q/Pmax Profiles | 23 | umax (400 kV) | 1.1 p.u. | 1.05 p.u. | 21.3.b (ii) | D PPMs | 3 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.3 | Article 21.3.b (i) and (ii) & Article 25.5: PPM: Parameters required for U-Q/Pmax Profiles | 23 | Qmin/Pmax (lead) (400 kV) | -0.5 p.u. | -0.33 p.u. | 21.3.b (ii) | D PPMs | 1 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.3 | Article 21.3.b (i) and (ii) & Article 25.5: PPM: Parameters required for U-Q/Pmax Profiles | 23 | Qmax/Pmax (lag) (400 kV) | 0.65 p.u. | 0.33 p.u. | 21.3.b (ii) | D PPMs | 1 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.3 | Article 21.3.b (i) and (ii) & Article 25.5: PPM: Parameters required for U-Q/Pmax Profiles | 24 | umin (Below 110kV ) | 0.875 p.u. | 0.94 pu | 21.3.b (ii) | C and D PPM | 1 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.3 | Article 21.3.b (i) and (ii) & Article 25.5: PPM: Parameters required for U-Q/Pmax Profiles | 24 | umax (Below 110kV ) | 1.1 p.u. | 1.06 pu | 21.3.b (ii) | C and D PPM | 1 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.3 | Article 21.3.b (i) and (ii) & Article 25.5: PPM: Parameters required for U-Q/Pmax Profiles | 24 | Qmin/Pmax (lead) (Below 110kV ) | -0.5 p.u. | -0.33 pu | 21.3.b (ii) | C and D PPM | 1 | parameter
Voltage Theme | Reactive Power Capability at Maximum Capacity: U-Q/Pmax Profiles | 4.2.2.2.3 | Article 21.3.b (i) and (ii) & Article 25.5: PPM: Parameters required for U-Q/Pmax Profiles | 24 | Qmax/Pmax (lag) (Below 110kV ) | 0.65 p.u. | 0.33 pu | 21.3.b (ii) | C and D PPM | 1 | parameter
Voltage Theme | Reactive Power Capability below Maximum Capacity: P-Q/Pmax Profiles | 4.2.2.3.1 | Article 21.3.c.(i), (ii) and (iv): PPM: Parameters required for P-Q/Pmax Profiles | 25 | pmin (110 - 400kV) | 0.0 p.u. | 0.12 p.u. | 21.3.c (ii) | D PPMs | 1 | parameter
Voltage Theme | Reactive Power Capability below Maximum Capacity: P-Q/Pmax Profiles | 4.2.2.3.1 | Article 21.3.c.(i), (ii) and (iv): PPM: Parameters required for P-Q/Pmax Profiles | 25 | pmax (110 - 400kV) | 1.0 p.u. | 1.0 p.u. | 21.3.c (ii) | D PPMs | 1 | parameter
Voltage Theme | Reactive Power Capability below Maximum Capacity: P-Q/Pmax Profiles | 4.2.2.3.1 | Article 21.3.c.(i), (ii) and (iv): PPM: Parameters required for P-Q/Pmax Profiles | 25 | Qmin/Pmax (lead) (110 - 400kV) | -0.5 p.u. | -0.33 p.u. | 21.3.c (ii) | D PPMs | 1 | parameter
Voltage Theme | Reactive Power Capability below Maximum Capacity: P-Q/Pmax Profiles | 4.2.2.3.1 | Article 21.3.c.(i), (ii) and (iv): PPM: Parameters required for P-Q/Pmax Profiles | 25 | Qmax/Pmax (lag) (110 - 400kV) | 0.65 p.u. | 0.33 p.u. | 21.3.c (ii) | D PPMs | 1 | parameter
Voltage Theme | Reactive Power Capability below Maximum Capacity: P-Q/Pmax Profiles | 4.2.2.3.1 | Article 21.3.c.(i), (ii) and (iv): PPM: Parameters required for P-Q/Pmax Profiles | 26 | pmin (Below 110kV) | 0.0 p.u. | 0.15 p.u. | 21.3.c (ii) | C and D PPM | 1 | parameter
Voltage Theme | Reactive Power Capability below Maximum Capacity: P-Q/Pmax Profiles | 4.2.2.3.1 | Article 21.3.c.(i), (ii) and (iv): PPM: Parameters required for P-Q/Pmax Profiles | 26 | pmax (Below 110kV) | 1.0 p.u. | 1.0 p.u. | 21.3.c (ii) | C and D PPM | 1 | parameter
Voltage Theme | Reactive Power Capability below Maximum Capacity: P-Q/Pmax Profiles | 4.2.2.3.1 | Article 21.3.c.(i), (ii) and (iv): PPM: Parameters required for P-Q/Pmax Profiles | 26 | Qmin/Pmax (lead) (Below 110kV) | -0.5 p.u. | -0.33 p.u. | 21.3.c (ii) | C and D PPM | 1 | parameter
Voltage Theme | Reactive Power Capability below Maximum Capacity: P-Q/Pmax Profiles | 4.2.2.3.1 | Article 21.3.c.(i), (ii) and (iv): PPM: Parameters required for P-Q/Pmax Profiles | 26 | Qmax/Pmax (lag) (Below 110kV) | 0.65 p.u. | 0.33 p.u. | 21.3.c (ii) | C and D PPM | 1 | parameter
Voltage Theme | Reactive Power Capability below Maximum Capacity: P-Q/Pmax Profiles | 4.2.2.3.2 | Article 21.3.c.(iv): PPM: Time to Achieve Target Value within P-Q/Pmax Profile | 27 | Time to achieve target value [transmission connected] | Not specified | Without delay but within 20 seconds | 21.3.c.(iv) | C and D SPGM | 3 | parameter
Voltage Theme | Reactive Power Capability below Maximum Capacity: P-Q/Pmax Profiles | 4.2.2.3.2 | Article 21.3.c.(iv): PPM: Time to Achieve Target Value within P-Q/Pmax Profile | 27 | Time to achieve target value [distribution connected] | Not specified | Without delay but within 20 seconds | 21.3.c.(iv) | C and D SPGM | 3 | parameter
Voltage Theme | Supplementary Reactive Power Requirements | 4.2.2.4.1 | Article 18.2.a: SPGM: Supplementary reactive power requirements | 28 | Right to specify supplementary reactive power requirements when the connection point is remote | To specify or not to specify | RSOs reserve the right to specify | 18.2.a | Type C and D SPGMs | 1 | requirement
Voltage Theme | Supplementary Reactive Power Requirements | 4.2.2.4.2 | Article 21.3.a: PPM: Supplementary reactive power requirements | 29 | Right to specify supplementary reactive power requirements when the connection point is remote | To specify or not to specify | RSOs reserve the right to specify | 21.3.a | Type C and D PPMs | 1 | requirement
Voltage Theme | Reactive Power Control Modes for PPMs | 4.2.3.1 | Article 21.3.d.(iv)- Voltage Control Mode | 30 | t1 = time within which 90% of the change in reactive power is reached | 1 – 5 sec | 1 | 21.3.d.(iv) | C and D PGMs | 1 | parameter
Voltage Theme | Reactive Power Control Modes for PPMs | 4.2.3.1 | Article 21.3.d.(iv)- Voltage Control Mode | 30 | t2 = time within which 100% of the change in reactive power is reached | 5 – 60 sec | 5 | 21.3.d.(iv) | C and D PGMs | 1 | parameter
Voltage Theme | Reactive Power Control Modes for PPMs | 4.2.3.2 | Article 21.3.d (vi) - Power Factor Control Mode | 31 | Target power factor | Not specified | site-specific | 21.3.d.(vi) | C and D PGMs | 3 | parameter
Voltage Theme | Reactive Power Control Modes for PPMs | 4.2.3.2 | Article 21.3.d (vi) - Power Factor Control Mode | 31 | Time period to reach the set point | Not specified | 5 seconds | 21.3.d.(vi) | C and D PGMs | 3 | parameter
Voltage Theme | Reactive Power Control Modes for PPMs | 4.2.3.2 | Article 21.3.d (vi) - Power Factor Control Mode | 31 | Tolerance | Not specified | 5% | 21.3.d.(vi) | C and D PGMs | 3 | parameter
Voltage Theme | Voltage Control System for SPGM | 4.2.4.1 | Article 19.2.a and 19.2.b.(v) | 32 | Power Threshold | Not specified | All Type D SPGMs | 19.2.b.(v) | D SPGMs | 2 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.1 | Article 14.3.a & 16.3.a: FRT Capability for PGMs connected at voltage level <110 kV | 33 | Uret | 0.05-0.3 | 0.05 | 14.3.a & 16.3.a | B, C, D SPGMs | 3 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.1 | Article 14.3.a & 16.3.a: FRT Capability for PGMs connected at voltage level <110 kV | 33 | Uclear | 0.7-0.9 | 0.7 | 14.3.a & 16.3.a | B, C, D SPGMs | 3 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.1 | Article 14.3.a & 16.3.a: FRT Capability for PGMs connected at voltage level <110 kV | 33 | Urec1 | Uclear | Uclear | 14.3.a & 16.3.a | B, C, D SPGMs | 3 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.1 | Article 14.3.a & 16.3.a: FRT Capability for PGMs connected at voltage level <110 kV | 33 | Urec2 | 0.85-0.9 & >=Uclear | 0.9 | 14.3.a & 16.3.a | B, C, D SPGMs | 3 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.1 | Article 14.3.a & 16.3.a: FRT Capability for PGMs connected at voltage level <110 kV | 33 | tclear | 0.14-0.25 | 0.15 | 14.3.a & 16.3.a | B, C, D SPGMs | 3 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.1 | Article 14.3.a & 16.3.a: FRT Capability for PGMs connected at voltage level <110 kV | 33 | trec1 | tclear | tclear | 14.3.a & 16.3.a | B, C, D SPGMs | 3 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.1 | Article 14.3.a & 16.3.a: FRT Capability for PGMs connected at voltage level <110 kV | 33 | trec2 | trec1-0.7 | 0.45 | 14.3.a & 16.3.a | B, C, D SPGMs | 3 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.1 | Article 14.3.a & 16.3.a: FRT Capability for PGMs connected at voltage level <110 kV | 33 | trec3 | trec2-1.5 | trec2 | 14.3.a & 16.3.a | B, C, D SPGMs | 3 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.1 | Article 14.3.a & 16.3.a: FRT Capability for PGMs connected at voltage level <110 kV | 34 | Uret | 0.05-0.15 | 0.15 | 14.3.a & 16.3.a | B, C, D PPMs and Offshore PPMs | 3 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.1 | Article 14.3.a & 16.3.a: FRT Capability for PGMs connected at voltage level <110 kV | 34 | Uclear | Uret -0.15 | 0.15 | 14.3.a & 16.3.a | B, C, D PPMs and Offshore PPMs | 3 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.1 | Article 14.3.a & 16.3.a: FRT Capability for PGMs connected at voltage level <110 kV | 34 | Urec1 | Uclear | Uclear | 14.3.a & 16.3.a | B, C, D PPMs and Offshore PPMs | 3 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.1 | Article 14.3.a & 16.3.a: FRT Capability for PGMs connected at voltage level <110 kV | 34 | Urec2 | 0.85 | 0.85 | 14.3.a & 16.3.a | B, C, D PPMs and Offshore PPMs | 3 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.1 | Article 14.3.a & 16.3.a: FRT Capability for PGMs connected at voltage level <110 kV | 34 | tclear | 0.14-0.25 | 0.25 | 14.3.a & 16.3.a | B, C, D PPMs and Offshore PPMs | 3 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.1 | Article 14.3.a & 16.3.a: FRT Capability for PGMs connected at voltage level <110 kV | 34 | trec1 | tclear | tclear | 14.3.a & 16.3.a | B, C, D PPMs and Offshore PPMs | 3 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.1 | Article 14.3.a & 16.3.a: FRT Capability for PGMs connected at voltage level <110 kV | 34 | trec2 | trec1 | tclear | 14.3.a & 16.3.a | B, C, D PPMs and Offshore PPMs | 3 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.1 | Article 14.3.a & 16.3.a: FRT Capability for PGMs connected at voltage level <110 kV | 34 | trec3 | 1.5-3.0 | 2.9 | 14.3.a & 16.3.a | B, C, D PPMs and Offshore PPMs | 3 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.2 | Article 16.3.a FRT Capability for PGMs connected at voltage level ³110 kV | 35 | Uret | 0 | 0 | 16.3.a | D SPGMs | 3 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.2 | Article 16.3.a FRT Capability for PGMs connected at voltage level ³110 kV | 35 | Uclear | 0.25 | 0.25 | 16.3.a | D SPGMs | 3 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.2 | Article 16.3.a FRT Capability for PGMs connected at voltage level ³110 kV | 35 | Urec1 | 0.5-0.7 | 0.5 | 16.3.a | D SPGMs | 3 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.2 | Article 16.3.a FRT Capability for PGMs connected at voltage level ³110 kV | 35 | Urec2 | 0.85-0.9 | 0.9 | 16.3.a | D SPGMs | 3 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.2 | Article 16.3.a FRT Capability for PGMs connected at voltage level ³110 kV | 35 | tclear | 0.14-0.25 | 0.15 | 16.3.a | D SPGMs | 3 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.2 | Article 16.3.a FRT Capability for PGMs connected at voltage level ³110 kV | 35 | trec1 | tclear -0.45 | tclear | 16.3.a | D SPGMs | 3 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.2 | Article 16.3.a FRT Capability for PGMs connected at voltage level ³110 kV | 35 | trec2 | trec1-0.7 | 0.45 | 16.3.a | D SPGMs | 3 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.2 | Article 16.3.a FRT Capability for PGMs connected at voltage level ³110 kV | 35 | trec3 | trec2-1.5 | trec2 | 16.3.a | D SPGMs | 3 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.2 | Article 16.3.a FRT Capability for PGMs connected at voltage level ³110 kV | 36 | Uret | 0 | 0 | 16.3.a | D PPMs | 1 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.2 | Article 16.3.a FRT Capability for PGMs connected at voltage level ³110 kV | 36 | Uclear | Uret | Uret | 16.3.a | D PPMs | 1 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.2 | Article 16.3.a FRT Capability for PGMs connected at voltage level ³110 kV | 36 | Urec1 | Uclear | Uclear | 16.3.a | D PPMs | 1 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.2 | Article 16.3.a FRT Capability for PGMs connected at voltage level ³110 kV | 36 | Urec2 | 0.85 | 0.85 | 16.3.a | D PPMs | 1 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.2 | Article 16.3.a FRT Capability for PGMs connected at voltage level ³110 kV | 36 | tclear | 0.14-0.25 | 0.15 | 16.3.a | D PPMs | 1 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.2 | Article 16.3.a FRT Capability for PGMs connected at voltage level ³110 kV | 36 | trec1 | tclear | tclear | 16.3.a | D PPMs | 1 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.2 | Article 16.3.a FRT Capability for PGMs connected at voltage level ³110 kV | 36 | trec2 | trec1 | tclear | 16.3.a | D PPMs | 1 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.2 | Article 16.3.a FRT Capability for PGMs connected at voltage level ³110 kV | 36 | trec3 | 1.5-3.0 | 2.9 | 16.3.a | D PPMs | 1 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.3.1 | Article 20.2.b Fast Fault Current Injection for Symmetrical Faults | 37 | Voltage threshold for fast fault current injection | Not specified | During voltage dips i.e. when the voltage is below 0.9 p.u. | 20.2.b | B, C and D PPMs | 1 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.3.1 | Article 20.2.b Fast Fault Current Injection for Symmetrical Faults | 37 | End of the voltage deviation | Not specified | Once the voltage has recovered to within normal operating voltage range | 20.2.b | B, C and D PPMs | 1 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.3.1 | Article 20.2.b Fast Fault Current Injection for Symmetrical Faults | 37 | the characteristics of the fast fault current, including the time domain for measuring the voltage deviation and fast fault current | Not specified | Reactive current should be provided for the duration of the voltage deviation within the rating of the PPM | 20.2.b | B, C and D PPMs | 1 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.3.1 | Article 20.2.b Fast Fault Current Injection for Symmetrical Faults | 37 | the timing and accuracy of the fast fault current, which may include several stages during a fault and after its clearance | Not specified | Rise Time no greater than 100ms and a Settling Time no greater than 300ms. | 20.2.b | B, C and D PPMs | 2 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.3.2 | Article 20.2.c Fast Fault Current Injection for Asymmetrical Faults | 38 | Voltage threshold for fast fault current injection | Not specified | During voltage dips i.e. when the voltage is below 0.9 p.u. | 20.2.b | B, C and D PPMs | 1 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.3.2 | Article 20.2.c Fast Fault Current Injection for Asymmetrical Faults | 38 | the characteristics of the fast fault current, including the time domain for measuring the voltage deviation and fast fault current | Not specified | Reactive current should be provided for the duration of the voltage deviation within the rating of the PPM | 20.2.b | B, C and D PPMs | 1 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.3.2 | Article 20.2.c Fast Fault Current Injection for Asymmetrical Faults | 38 | the timing and accuracy of the fast fault current, which may include several stages during a fault and after its clearance | Not specified | Rise Time no greater than 100ms and a Settling Time no greater than 300ms. | 20.2.b | B, C and D PPMs | 2 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.4 | Article 20.3.a Post-Fault Active Power Recovery for PPMs | 39 | when the post-fault active power recovery begins, based on a voltage criterion | Not specified | un< 0.9 p.u. | 20.3.a | B, C and D PPMs and Offshore PPMs | 1 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.4 | Article 20.3.a Post-Fault Active Power Recovery for PPMs | 39 | maximum allowed time for active power recovery | Not specified | 500ms/1s | 20.3.a | B, C and D PPMs and Offshore PPMs | 1 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.4 | Article 20.3.a Post-Fault Active Power Recovery for PPMs | 39 | magnitude and accuracy for active power recovery | Not specified | 90% | 20.3.a | B, C and D PPMs and Offshore PPMs | 1 | parameter
Voltage Theme | Fault Ride Through Capability | 4.2.5.5 | Article 21.3.e Priority Given to Active or Reactive Power Contribution for PPMs | 40 | Prioritisation requirements during FRT | Active/Reactive | Active | 21.3.e | C and D PPMs and Offshore PPMs | 3 | parameter
Voltage Theme | Non-Mandatory Voltage Theme Requirements that we are not invoking at this time | 4.2.6 | Non-Mandatory Voltage Theme Requirements that we are not invoking at this time | 41 | Simultaneous overvoltage and underfrequency or simultaneous undervoltage and overfrequency | Do we want to expertise the right to specify this non-mandatory RfG? | Not invoking | 16(02)(a)(ii) | Type A, B, C and D PGMs |  | requirement
System Restoration Theme | Operation following Tripping to House Load | 4.3.1 | Article 15.5.c.(iii) Operation following tripping to house load | 42 | Operation Following Tripping to House Load | Not Specified | 4 hours | 15.5.c.iii | C and D PGMs and Offshore PPMs with a minimum re-synchronisation time greater than 15 minutes* | 3 | parameter
Protection and Instrumentation Theme | Manual, local measures where the automatic remote devices are out of service | 4.4.1 | Article 15.2.b: Manual, local measures where the automatic remote devices are out of service | 43 | Time required to achieve setpoint when automatic remote devices are unavailable | Not Specified | 1 hour | 15(2)(b) | B, C and D PGMs | 3 | parameter
Protection and Instrumentation Theme | Instrumentation: Quality of Supplies | 4.4.2 | Article 15.6.b (i): Instrumentation: Quality of Supplies | 44 | Quality of supplies parameters to be recorded. | Not Specified | Site Specific | 15(6)(b)(i) | C and D PGMs and Offshore PPMs | 1 | requirement
Protection and Instrumentation Theme | Dynamic System Behaviour Monitoring | 4.4.3 | Article 15.6.b.(iii): Dynamic System Behaviour Monitoring | 45 | oscillation trigger detecting poorly damped power oscillations. | Not Specified | Site Specific | 15(6)(b)(iii) | C and D PGMs and Offshore PPMs | 1 | parameter
Protection and Instrumentation Theme | Simulation Model Provision | 4.4.4 | Article 15.6.c.(iii) Simulation Model Provision | 46 | Model Provision | Not Specified | Retain the existing model provision requirements with the inclusion of min and max short circuit levels as part of Grid Code Planning Code Appendix Generator Data Requirements | 15(6)(c)(iii) | C and D PGMs and Offshore PPMs | 2 | requirement
Protection and Instrumentation Theme | Neutral-point at the network side of step transformers | 4.4.5 | Article 15.6.f.: Neutral-point at the network side of step transformers | 47 | Earthing arrangement of the neutral-point | Not Specified | Site specific - Will be specified as a part of the connection agreement | 15(6)(f) | C and D PGMs and Offshore PPMs | 1 | parameter
Protection and Instrumentation Theme | Non-Mandatory Protection Theme Requirements that are not for consultation but will be agreed on a case by case basis | 4.4.6 | Non-Mandatory Protection Theme Requirements that are not for consultation but will be agreed on a case by case basis | 48 | Control Scheme and Settings: Agreement and coordination between the TSO, the RSO (TSO and DSO) and the power generating facility owner (PGFO) | Control schemes and settings of the control devices | Case by case basis | 14.5.a | B,C,D PGMs and Offshore PPMs | N/A | parameter
Protection and Instrumentation Theme | Non-Mandatory Protection Theme Requirements that are not for consultation but will be agreed on a case by case basis | 4.4.6 | Non-Mandatory Protection Theme Requirements that are not for consultation but will be agreed on a case by case basis | 48 | Electrical Protection Schemes and settings: Agreement and coordination between the RSO and the PGFO | Protection schemes and settings | Case by case basis | 14.5.b | B,C,D PGMs and Offshore PPMs | N/A | parameter
Protection and Instrumentation Theme | Non-Mandatory Protection Theme Requirements that are not for consultation but will be agreed on a case by case basis | 4.4.6 | Non-Mandatory Protection Theme Requirements that are not for consultation but will be agreed on a case by case basis | 48 | Loss of angular stability or loss of control: Agreement between PGFO and the RSO (DSO or TSO), in coordination with the TSO | Criteria to detect loss of angular stability or loss of control | Case by case basis | 15.6.a | C.D PGMs and Offshore PPMs | N/A | parameter
Protection and Instrumentation Theme | Non-Mandatory Protection Theme Requirements that are not for consultation but will be agreed on a case by case basis | 4.4.6 | Non-Mandatory Protection Theme Requirements that are not for consultation but will be agreed on a case by case basis | 48 | Instrumentation: Settings of the fault recording equipment, including triggering criteria and sampling rate | Settings of the fault recording equipment, including triggering criteria and sampling rate | Case by case basis | 15.6.b(ii) | C, D PGMs and Offshore PPMs | N/A | parameter
Protection and Instrumentation Theme | Non-Mandatory Protection Theme Requirements that are not for consultation but will be agreed on a case by case basis | 4.4.6 | Non-Mandatory Protection Theme Requirements that are not for consultation but will be agreed on a case by case basis | 48 | Agreement between the PGFO and the RSO (DSO or TSO), in coordination with the TSO. |  | Case by case basis | 15.6.b(ii) | C, D PGMs and Offshore PPMs | N/A | parameter
Protection and Instrumentation Theme | Non-Mandatory Protection Theme Requirements that are not for consultation but will be agreed on a case by case basis | 4.4.6 | Non-Mandatory Protection Theme Requirements that are not for consultation but will be agreed on a case by case basis | 48 | Instrumentation: Protocols for recorded data | Protocols for recorded data | Case by case basis | 15.6.b(iv) | C, D PGMs and Offshore PPMs | N/A | parameter
Protection and Instrumentation Theme | Non-Mandatory Protection Theme Requirements that are not for consultation but will be agreed on a case by case basis | 4.4.6 | Non-Mandatory Protection Theme Requirements that are not for consultation but will be agreed on a case by case basis | 48 | Agreement between PGFO, the RSO and the relevant TSO |  | Case by case basis | 15.6.b(iv) | C, D PGMs and Offshore PPMs | N/A | parameter
Protection and Instrumentation Theme | Non-Mandatory Protection Theme Requirements that are not for consultation but will be agreed on a case by case basis | 4.4.6 | Non-Mandatory Protection Theme Requirements that are not for consultation but will be agreed on a case by case basis | 48 | Installation of devices for system operations and system security: Agreement between RSO or TSO and PGFO | Definition of the devices needed for system operation and system security | Case by case basis | 15.6.d | C, D PGMs and Offshore PPMs | N/A | parameter
Protection and Instrumentation Theme | Non-Mandatory Protection Theme Requirements that are not for consultation but will be agreed on a case by case basis | 4.4.6 | Non-Mandatory Protection Theme Requirements that are not for consultation but will be agreed on a case by case basis | 48 | Synchronisation: Agreement between the RSO and the PGFO | Settings of the synchronisation devices | Case by case basis | 16.4 | D PGMs and Offshore PPMs | N/A | parameter
Protection and Instrumentation Theme | Non-Mandatory Protection Theme Requirements that are not for consultation but will be agreed on a case by case basis | 4.4.6 | Non-Mandatory Protection Theme Requirements that are not for consultation but will be agreed on a case by case basis | 48 | Angular stability under fault conditions: Agreement between the TSO and PGFO | Agreement for technical capabilities of the power generating module to aid angular stability. | Case by case basis | 19.3 | D SPGM | N/A | parameter