## PPB SS Drafting Comments
DS3 System Services Agreement Consultation Comments - PPB
Section/Schedule | Section/Clause | Sub-section/ Sub-clause | Comment | Legal/Technical? | TSO Response
1 | Definitions and Interpretation
2 | Commencement and Duration of Agreement and Appointment to Framework
3 | Provision and Purchase of DS3 System Services | 3.5 | Outage Planning should be in accordance with Grid Code, stating that it should be Good Industry Practice introduces a new term which only brings confusion on what is required. | Technical | This clause has not changed from the existing EirGrid and SONI standard HAS agreements. In addition, as for DS3 System Services some of the providers/services will not be subject to the Grid Code, the TSOs believe that "Good Industry Practice" is appropriate.
4 | Payment
5 | Monitoring and Metering
6 | Assignment
7 | Variations
8 | Termination | 8.2 | The clause from the HAS in relation to damage or destruction of the generator should be included. | Legal | This clause has been added to 8.2.
9 | Effect of Termination
10 | Force Majeure
11 | Limitation of Liability
12 | Confidentiality
13 | Additional Costs
14 | Dispute Resolution
15 | Miscellaneous
16 | Governing Law and Jurisdictions
SCHEDULE 1 | Definitions |  | Lots of definitions are omitted due to the performance assessment being included in the Protocol document or not detailed at all in either. These calculations and definitions need to be added e.g. Frequency Event is no longer defined, this is an important parameter and must be defined and used as part of the operating reserve performance assessment. It is expected that all definitions contained in the HAS should be included in this agreement and more as there are additional services not less. | Technical | The assessment of reserve expected vs. reserve achieved has now been added to the Protocol. The appropriate defintions are included in the Protocol's glossary.
SCHEDULE 2 | Operating Reserves
Section 1 Operating Reserve Services
Section 2 Minimum Technical Requirements
| Section 3 Primary Operating Reserve (POR) - Available Volume, Payment and Performance Assessment | 3.1 (b) 3.2 (c ) | 3.1 (b) It would be helpful to add the wording in the trading period to this definition. 3.2 (c) POR Product Scalar needs defined. | Technical | 3.1(b) in the TP is implicit in "Declared" and the first line of 3.1. "Product Scalar" is defined. Product Scalar and POR are separately defined.
| Section 4 Secondary Operating Reserve (SOR) - Available Volume, Payment and Performance Assessment | 4.1 (b) 4.2 (c ) | 4.1 (b) It would be helpful to add the wording in the trading period to this definition. 4.2 (c) POR Product Scalar needs defined. | Technical | 4.1(b) in the TP is implicit in "Declared" and the first line of 4.1. "Product Scalar" is defined. Product Scalar and SOR are separately defined.
| Section 5 Tertiary 1 Operating Reserve (TOR1) - Available Volume, Payment and Performance Assessment | 5.1 (b) 5.2 (c ) | 5.1 (b) It would be helpful to add the wording in the trading period to this definition. 5.2 (c) POR Product Scalar needs defined. | Technical | 5.1(b) in the TP is implicit in "Declared" and the first line of 5.1. "Product Scalar" is defined. Product Scalar and TOR1 are separately defined.
| Section 6 Tertiary 2 Operating Reserve (TOR2) - Available Volume, Payment and Performance Assessment | 6.1 (b) 6.2 (c ) | 6.1 (b) It would be helpful to add the wording in the trading period to this definition. 6.2 (c) POR Product Scalar needs defined. | Technical | 6.1(b) in the TP is implicit in "Declared" and the first line of 6.1. "Product Scalar" is defined. Product Scalar and TOR2 are separately defined.
Section 7 Replacement Reserve - Available Volume, Payment and Performance Assessment
SCHEDULE 3 | Steady-State Reactive Power
Section 1 Provision of Service
Section 2 Minimum Technical Requirements
Section 3 Steady-State Reactive Power - Available Volume, Payment and Performance Assessment
SCHEDULE 4 | Other Services
SCHEDULE 4 - Part A | Section 1 Definition of Service
Section 2 Minimum Technical Requirements
Section 3 Synchronous Inertial Response - Available Volume and Payment
SCHEDULE 4 - Part B | Section 1 Definition of Service
Section 2 Minimum Technical Requirements
Section 3 Fast Frequency Response - Available Volume, Payment and Performance Assessment
SCHEDULE 4 - Part C | Section 1 Definition of Service
Section 2 Minimum Technical Requirements
Section 3 Fast Post-Fault Active Power Recovery - Available Volume, Payment and Performance Assessment
SCHEDULE 4 - Part D | Section 1 Definition of Service |  | The definition should be made clearer as the MW reduction can be confused with deloading provided with a generator or demand reduction as provided with a demand side unit. | Technical | MW Reduction is defined as a reduction in Demand as opposed to generation, where Demand is as defined in the Grid Code.
| Section 2 Minimum Technical Requirements |  | Should say Part D | Typo | Yes, the TSOs agree. This should read Part D of Schedule 4 and has been amended.
| Section 3 Ramping Margin 1 (RM1) – Available Volume, Payment and Performance Assessment |  | Declared RM1 is not clearly defined. | Technical | "Declared" and "RM1" are both defined separately. Therefore Declared RM1 is defined.
| Section 4 Ramping Margin 3 (RM3) – Available Volume, Payment and Performance Assessment |  | Declared RM3 is not clearly defined. | Technical | "Declared" and "RM3" are both defined separately. Therefore Declared RM3 is defined.
| Section 5 Ramping Margin 8 (RM8) - Available Volume, Payment and Performance Assessment |  | Declared RM8 is not clearly defined. | Technical | "Declared" and "RM8" are both defined separately. Therefore Declared RM8 is defined.
SCHEDULE 4 - Part E | Section 1 Definition of Service
Section 2 Minimum Technical Requirements
Section 3 Dynamic Reactive Response (DRR) - Available Volume, Payment and Performance Assessment
SCHEDULE 5 | Billing and Payment Plan |  | Should be aligned with NI. | Technical | An extensive response to this is given in the answer to Q9 of the consultation.
SCHEDULE 6 | Dispute Resolution Procedure
SCHEDULE 7 | Address Details and Billing Address
SCHEDULE 8 | Banking Details of the Service Provider
SCHEDULE 9 | Providing Unit and Operating Parameters |  | This section has much less information than the current HAS agreements. It is important that it has all the detail included to prevent any disparity in requirements and subsequent settlement. | Technical | The TSOs do not believe that this is the case. The information is presented in a different way in some instances. There is nothing to preclude additional information being inserted into Schedule 9 for individual Providing Units. - e.g. The TSOs have not put multiple reserve characteristics into a generic contract but this may be done, where appropriate for individual Providing Units. The updated Schedule 9 includes more information.
| Additional Comment |  | The text has not been exhaustively critiqued due to considerable rewording of the clauses being required for Intermedaries along with all the detail on Performance Monitoring which is missing from both the Protocol and framework Agreement. | Technical/Legal Intermediaries | An amended contract for intermediaries has been drafted. The detail of performance monitoring is contained in the Protocol document.

## ESB-GWM SS Drafting Comments
DS3 System Services Agreement Consultation Comments - ESB Generation and Wholesale Markets
Section/Schedule | Section/Clause | Sub-section/ Sub-clause | Comment | Legal/Technical? | TSOs' Response
1 | Definitions and Interpretation |  | No comments
2 | Commencement and Duration of Agreement and Appointment to Framework | 2.1 Term of Agreement & Definitions | There is an inconsistency with the current definition of "Term" and Clause 2.1 which is drafted assuming a fixed term with TSO optional extension of 18 months. Also, given that the interim arrangements is providing a mechanism to establish the characteristics of new technologies, the Service Provider should have some options where it would be reasonable for it reject the extension. In addition "or for any other reason whatever" should be deleted from 2.1.2. | Legal | The clauses relating to the term of the Framework Agreement (2.1.1 and 2.1.2 have been re-drafted).
|  | 2.4 Appointment | Why was it necessary to change the legal provisions here? Preference is to revert to existing template wording, some of these amendments are significant which is contrary to TSO's suggestion that only minor amendments to the legal provisions have been made. At the very least clause 2.4.3 should be deleted as liability is already adequately provided for in clause 11, similarly 2.4.4 is not necessary for a framework agreement. | Legal | Clauses 2.4.3 and 2.4.4 have been deleted.
|  | 2.5 Availability of Services | This is unnecessary and should be deleted. Already adequately covered elsewhere, e.g., provision & purchase in clause 3 & payment for availability in section 4. | Legal | This clause sets out the overall terms of the framework and has therefore been retained.
|  | 2.6 Implementation of Services | Again, this is unnecessary and should be deleted. The 'immediate implementation' wording implies an obligation to provide the contracted services regardless of the operational status or plant availability. The availability and performance of the service following the TSO request for same is already adequately covered through the existing clause, Schedules for the services and the payment rights arising. | Legal | This section sets out the framework agreement in broad principles, i.e. that service providers could be called upon to provide DS3 System Services. The TSOs believe that it should be retained.
|  | 2.8 Payment | Payment is already covered in section 4 and should not be covered here | Legal | Section 2.8 Payment has been deleted.
3 | Provision and Purchase of DS3 System Services |  | No comments
4 | Payment |  | No comments
5 | Monitoring and Metering |  | Performance monitoring should be included in the body of the Framework Agreement rather than in the Protocol document unless it is intended that Protocol document won't be subject to amendment without industry consultation and approval of the Regulatory Authorities. | Technical/Legal | The TSOs believe that performance monitoring should be detailed in the Protocol document, as discussed more fully in the answer to Q6 in the consultation decision paper.
6 | Assignment |  | No comments
7 | Variations |  | No comments
8 | Termination | 8.1 | Termination for convenience for interim framework agreement of finite term is inappropriate. Termination might be reasonable during the extended term (per proposed clause 2.1.2) provided such termination related to the earlier than expected introduction of the replacement Framework Agreement and/or DSC System Services. | Legal | The TSOs believe that the termination clause should remain as drafted. A more detailed explanation of this is given in the answer to Q4 in the consultation decision paper.
|  | 8.3 | Clause 8.3 should also allow the Service Provider to terminate individual services, rather than just the whole agreement. | Legal | HAS does not currently allow this. The TSOs believe that the clause should remain as drafted.
9 | Effect of Termination |  | No comments |  |  | .
10 | Force Majeure | 10.1 | No comments
11 | Limitation of Liability |  | No comments
12 | Confidentiality |  | No comments
13 | Additional Costs |  | No comments
14 | Dispute Resolution | Schedule 6 | Why maintain separate Dispute Resolution procedures? The differences here are quite significant, i.e., one allows for arbitration, the other does not. If separate Dispute Resolution procedures can be maintained surely same can be said for other differences, e.g., Billing & Payment Plans. Also, there should be no reason why timelines could not be aligned. | Legal | The reasons for aligning Settlement and Billing between Ireland and Northern Ireland are clearly addressed in the TSOs' response to Q9 in the decision paper. The Dispute Resolution Procedures are quite different, as pointed out by the respondent. The TSOs will examine the possibility of aligning them for the enduring arrangements. However, it is not necessary from a settlement system perspective, unlike billing and settlement.
15 | Miscellaneous |  | No comments
16 | Governing Law and Jurisdictions |  | No comments
SCHEDULE 1 | Definitions | "Automatic Voltage Regulation Status or AVR Status" | This is not further defined in Section 3.2 of Schedule 3 as suggested. Also, the AVR Status should be set to 1 when the AVR is activated, or otherwise zero. | Technical | It is further defined in Section 3.2 and has also been amended for clarity with reference to other comments.
|  | Connection Point | The connection point for Interconnectors in respect of all DS3 System Services should be the point of physical connection to the Power System in Ireland/Northern Ireland, not the physical connection point to the GB Power System. This will help promote equality between interconnectors and other service providers in the provision of DS3 System Services. | Technical | The TSOs believe that the proposed definition is appropriate. Within the SEM, the point of connection of Interconnectors is defined as being at the remote end of the Interconnector i.e. at the GB side. The definition of Connection Point for Interconnectors for DS3 System Services aligns with this for all services except SSRP, DRR (both of which are reactive power services) and FPFAPR. The active power i.e. MW control system for the interconnectors which controls the power flow is referenced at one point, the GB reference point, to control the market flows. The DS3 SS active power services such as reserve operate with activation of the control system which is referenced at GB. The reactive power services (SSRP and DRR) can be controlled locally at either end hence they are provided at the Ireland and Northern Ireland ends. The FPFAPR is an automatic function of the link controls that effect both ends and can be assessed at the Ireland/ NI end. Provision of these 3 services (SSRP, DRR and FPFAPR) at the remote end of the interconnectors (GB) would provide no benefit to the Irish power system. Therefore for these 3 services, the Interconnector Connection Point is defined as being the physical point where the Interconnector is joined to the Power System of Ireland or Northern Ireland as appropriate.
|  | "Declared Automatic Voltage Regulation Status or AVR Status" | The AVR Status is not notified under SDC1 of the Grid Code | Technical | This definition has now been amended.
|  | "Protocol" | Protocol should be defined by a particular date. Performance monitoring, reliability target and associated scalar calculations could materially impact on the revenues and should be fixed for the duration of the contract. We suggest performance monitoring should actually be included within the body of the agrreement rather than in the Protocol. If performance monitoring is included in the Protocol, changes should only be permitted on contract renewal and/or subject to industry consultation and approval by the Regulatory Authorities. | Technical/Legal | The Protocol document is not defined by a particular date, as the most recent published version is the one in force.
|  | "Reserve Step Sizes" and "Reserve Step Triggers" | Reserve step sizes and associated triggers would be specified in the tender by the Service Provider rather than be set by the TSO | Technical | Service Providers inform the TSOs of their capability. The TSOs then set these parameters based on the Service Providers' capability.
|  | "Term" | should be amended to read "means a term of twelve (12) months commencing on the date specified in clause 2.1.1." | Legal | The definition of "Term" has been deleted in line with the amendment of clause 2.1.
SCHEDULE 2 | Operating Reserves
| Section 1 Operating Reserve Services |  | No comments
| Section 2 Minimum Technical Requirements | Section 2, Para 1 | Some units may not be capable of providing the technical requirements specified in the Grid Code and have a derogation in place - this clause should point to the contracted volumes (Operating Parameters) and not Grid Code requirements. | Technical | This clause is taken from HAS. The Minimum Techncial Requirements section is used to define the service. The existing system (ancillary) services are defined in the Grid Code, while the new system services are defined explicity in their respective Minimum Techncial Requirements sections.
|  | Section 2, Para 2 | There is no need to define Replacement Reserve here - its covered in the definitions | Technical | Where a service is not defined in the Grid Code (or is defined differently as in this case), it is defined in the early sections of the schedule.
|  | Section 2, Para 4 | Scope to change Reserve Triggers, Droop and Step Sizes are likely to be unit dependent, especially for DSUs. This clause should recognise that the scope to change these within the contracted parameters may be limited. Also, trigger points and steps sizes may be 'hard wired', and changing these within 60 seconds may not be feasible for many service providers. | Technical | The TSOs require this level of flexibility from service providers. We do not want trigger points and step sizes to be hard-wired. This may be challenging for service providers, but will form part of the service provided.
| Section 3 Primary Operating Reserve (POR) - Available Volume, Payment and Performance Assessment |  | No comments
| Section 4 Secondary Operating Reserve (SOR) - Available Volume, Payment and Performance Assessment |  | No comments
| Section 5 Tertiary 1 Operating Reserve (TOR1) - Available Volume, Payment and Performance Assessment | Section 5.2 | In TOR1 timescales , there is limited distinction between the provision of static and dynamic response. Reserves needed in these timescales are more likely to be for ongoing operational issues, which can equally be provided by static and dynamic sources. We therefore suggest the simplification of removing the TOR Product Scalar and associated definitions (consistent with TOR2). | Technical | The TOR1 Product scalar is defined based on the TSOs' operational needs.
| Section 6 Tertiary 2 Operating Reserve (TOR2) - Available Volume, Payment and Performance Assessment |  | No comments
| Section 7 Replacement Reserve - Available Volume, Payment and Performance Assessment |  | No comments
SCHEDULE 3 | Steady-State Reactive Power
| Section 1 Provision of Service |  | No comments
| Section 2 Minimum Technical Requirements |  | Some units may not be capable of providing the technical requirements specified in the Grid Code and have a derogation in place - this clause should point to the contracted service capability (Operating Parameters) rather than Grid Code requirements. | Technical | This clause is taken from HAS. The Minimum Techncial Requirements section is used to define the service. The existing system (ancillary) services are defined in the Grid Code, while the new system services are defined explicity in their respective Minimum Techncial Requirements sections.
| Section 3 Steady-State Reactive Power - Available Volume, Payment and Performance Assessment | Section 3.1 - Reactive Power Available Volume | In defining SSRP MinGen, "Minimum MW Output" is not a defined term in the contract. We suggest simplifying so that SSRP MinGen becomes a fixed parameter in the contract established during the tender process. | Technical/Legal | The TSOs agree with this point. The definition of SSRP MinGen has been amended to account for this.
|  | Section 3.2 - SSRP Payment | It may be helpful to define the Declared Automatic Voltage Regulator Status and a number between 0 and 1 representing the proportion of time during the Trading Period that the AVR associated with the Providing Unit is activated. | Technical | The SSRP Product Scalar definition has been amended to reflect its numerical value.
SCHEDULE 4 | Other Services
SCHEDULE 4 - Part A | Section 1 Definition of Service |  | No comments
| Section 2 Minimum Technical Requirements |  | No comments
| Section 3 Synchronous Inertial Response - Available Volume and Payment | Section 3.2 | Payment should be for each MWs2, rather than each MW | Technical | Yes, the TSOs agree. We have amended the framework agreements accordingly.
SCHEDULE 4 - Part B | Section 1 Definition of Service |  | No comments
| Section 2 Minimum Technical Requirements |  | No comments
| Section 3 Fast Frequency Response - Available Volume, Payment and Performance Assessment | Section 3.2 | Remove references to the "FFR Performance Scalar" - Section 4.5 of the Protocol states that "The three fast-acting DS3 System Services (FFR, FPFAPR and DDR) will not be subject to the interim performance monitoring arrangements..", nor is there a methodology set out in in Table 2 for calculating a Performance Scalar for these services. | Technical | It is correct that FFR will not have a performance scalar inthe Interim Arrangements. This was included to account for the future enduring arrangements when FFR will have a performance scalar. The FFR Performance Scalar will be set = 1 for the Interim Arrangements. The Protocol has been updated to reflect this.
SCHEDULE 4 - Part C | Section 1 Definition of Service |  | No comments
| Section 2 Minimum Technical Requirements |  | No comments
| Section 3 Fast Post-Fault Active Power Recovery - Available Volume, Payment and Performance Assessment | Section 3.1 - FPFAPR Available Volume | "Declared Availability" in respect of this service is not a defined term. | Technical | Declared and Availability are both defined separately. Therefore Declared Availability is a defined term.
|  | Section 3.2 - FPFAPR Payments | Remove references to the "FPFAPR Performance Scalar" - Section 4.5 of the Protocol states that "The three fast-acting DS3 System Services ( FFR, FPFAPR and DDR) will not be subject to the interim performance monitoring arrangements..", nor is there a methodology set out in in Table 2 for calculating a Performance Scalar for these services | Technical | It is correct that FPFAPR will not have a performance scalar for the Interim Arrangements. This was left in to account for the future enduring arrangements when FPFAPR will have a performance scalar. The FFR Performance Scalar will be set = 1 for the interim arrangements. The Protocol has been updated to reflect this.
SCHEDULE 4 - Part D | Section 1 Definition of Service |  | No comments
| Section 2 Minimum Technical Requirements |  | No comments
| Section 3 Ramping Margin 1 (RM1) – Available Volume, Payment and Performance Assessment | Section 3.1 - RM1 Availability Volume | The increased MW Output a Providing Unit can provide will depend on the heat state of the unit. Is the intention that the 'Potential Ramping Margin' will be based on the unit being hot, given that the heat state (and therefore the actual availability of RM1) will be driven by TSO dispatch decisions? The definition should clarify this point. | Technical | The definition of Potential Ramping Margin has been amended to include "as determined by its warmth state as appropriate".
|  | Section 3.1 (b) | For average MW reduction, the baseline for this calculation should be set out - e.g. average demand for the same period in the previous 5 working days. | Technical | This calculation will be based on DSU SCADA data.
| Section 4 Ramping Margin 3 (RM3) – Available Volume, Payment and Performance Assessment | Section 4.1 - RM8 Availability Volume | Same comments as for RM1 | Technical | The same response as above applies.
| Section 5 Ramping Margin 8 (RM8) - Available Volume, Payment and Performance Assessment | Section 5.1 - RM8 Availability Volume | Same comments as for RM1 | Technical | The same response as above applies.
SCHEDULE 4 - Part E | Section 1 Definition of Service |  | No comments
| Section 2 Minimum Technical Requirements |  | No comments
| Section 3 Dynamic Reactive Response (DRR) - Available Volume, Payment and Performance Assessment | Section 3.1 - DDR Available Volume | This should not be the product of the Reg Cap and the Declared DRR. To be consistent with the DS3 Technical Definitions decision paper, the DRR Available Volume should be based on the Registered Capacity of the unit for the percentage of the Trading Period in which the unit is synchronised. | Technical | As per 4.7.14 of the consultation decision paper, the definition of the DRR Available Volume is consistent with SEM Committee Decision SEM-13-098. For clarity, the Time-Weighted Average of Declared DRR will have a value between 0 and 1. Declared DRR will be 1 when the Providing Unit is synchronised or connected to the power system and 0 when it is not. The Providing Unit may be synchronised or connected to the power system for part of a Trading Period, in which case the Time-Weighted Average of Declared DRR will have a value greater than 0 and less than 1.
|  | Section 3.2 - DDR Payments | Remove references to the "DRR Performance Scalar" - Section 4.5 of the Protocol states that "The three fast-acting DS3 System Services (FFR, FPFAPR and DDR) will not be subject to the interim performance monitoring arrangements..", nor is there a methodology set out in in Table 2 for calculating a Performance Scalar for these services. | Technical | It is correct that DRR will not have a performance scalar in the Interim Arrangements. This was left in to account for the future enduring arrangements when FPFAPR will have a performance scalar. The FFR Performance Scalar will be set = 1 for the Interim Arrangements. The Protocol has been updated to reflect this.
SCHEDULE 5 | Billing and Payment Plan | Daily Confirmation Sheets | Removing the requirement for Daily Confirmation sheets by D+3 is a backward step. These should be restored to the SONI agreement and introduced to the EirGrid agreement. A continuous flow of information on volumes and performance will be essential to the success of the DS3 System Services and should be made a permanent feature of the enduring arrangements. They will also allow billing issues to be identified and resolved ahead of the formal billing process, and performance issues to be highlighted and resolved early. | Technical | The reasons for the alignment of billing and settlement timelines between Ireland and Northern Ireland are explained in the answer to Q9 of the consultation decision paper.
|  | Statement of Account and Invoicing - Section 1 | The proposal to have separate Framework Agreements for each Providing Unit would result in multiple Statement of Accounts and Invoices for some Service Providers. We suggest that clause is amended to allow a single monthly Statement of Account and Invoice to cover all Providing Units for each Service Provider/TSO. This will reduce the administrative overhead for the TSOs and Service Providers with multiple Providing Units and reduce the changes necessary to respective billing systems. | Technical | The TSOs currently and plan to continue to issue a report and invoices at a service provider level in each TSO. All references in Schedule 5 are on a service provider rather than a Providing Unit level.
|  | Statement of Account and Invoicing - Section 1.5 | Is this section 1.5 intended to replace the existing 3.2-3.7? This is a significant change to the obligations and rights of the parties for which TSO has given no justification. We believe it is improperly drafted and in any event, unnecessary for the purposes of the interim framework. It should be struck out. However, we appreciate that parties will want finality to payment disputes arising under the interim framework and would suggest a period of 2 years following the termination of the framework agreement as being reasonable. | Legal | The TSOs are of the view that one year is sufficient time for a Service Provider to identify and raise a dispute and that it is in the interests of the TSOs, Service Providers and end consumers that the financial accounts in relation to the interim arrangements are finalised within a reasonable time period.
|  | Billing and Payment Reconciliation and Dispute Resolution Mechanism - Section 3 | Sections 3.2 to 3.7 of the current HAS agreement dealing with Billing and Payment Reconciliation should be retained in the contract. Metering / measurement errors and other issues take time to emerge and a reconciliation process is required to deal with any inaccuracies that come to light after the monthly Statements of Accounts are issued and the associated Invoices paid. | Legal | As noted in 4.9.6 of the decision paper, these clauses relate to yearly reconciliation, which while detailed in the current EirGrid HAS agreement, has never been used in practice and had therefore been removed as a redundant process for DS3 System Services. The TSOs intend to address all resettlement issues on a monthly basis. A dispute of statement process is included in clause 3.1 of Schedule 5 and in the case of a disputed statement that remains unresolved 40 business days after the receipt of the claim, Service Providers have recourse to the Dispute Resolution mechanism in Schedule 6.
SCHEDULE 6 | Dispute Resolution Procedure | Clause 14 | See comments at 14 [Dispute Resolution]. | Legal | Please see response on Dispute Resolution Procedure.
SCHEDULE 7 | Address Details and Billing Address |  | No comments
SCHEDULE 8 | Banking Details of the Service Provider |  | No comments
SCHEDULE 9 | Providing Unit and Operating Parameters |  | No comments

## AES SS Drafting Comments
DS3 System Services Agreement Consultation Comments - AES
Section/Schedule | Section/Clause | Sub-section/ Sub-clause | Comment | Legal/Technical? | TSOs' Response
1 | Definitions and Interpretation | Recital C and D | "Tender" is referred to in Recital C but not defined. Recital C and D are very similar - is there a need for both? | Legal | "Tender" has been defined. Recitals C and D have been amalgamated.
2 | Commencement and Duration of Agreement and Appointment to Framework | Clause 2.1.1 & Clause 2.1.2 & Clause 2.4.3 & Clause 2.6.2 | Clause 2.1.1 - This drafting is confusing and circular. Please revisit the definition of "Term" and propose clearer drafting. One solution would be to delete the definition of "Term" and simply say that the agreement continues for a period of at least 12 months from DS3 System Services Go-Live and ends when terminated by either Party in accordance with Clause 8. Clause 2.1.2 - "Frameworks" is capitalised but not defined. Clause 2.4.3 - please delete Clause 2.6.2 - in the penultimate line after, "the Company" add the words "(and agreed by the Service Provider)" | Legal | "Term" has been deleted and clause 2.1.1 has been amended. Clause 2.4.3 has been deleted. The TSOs do not believe that it is appropriate to amend clause 2.6.2.
3 | Provision and Purchase of DS3 System Services | Clause 3.1.2(ii) | Add at end of clause 3.1.2(ii) "(which shall include where there has been a recommendation to the Service Provider to that effect by the relevant original equipment manfacturer of the Providing Unit)" New clause 3.6 to be added to state that "Nothing in this Agreement shall require the Service Provider to operate the Providing Unit in such a manner so as to breach its obligations under any health and safety legislation or environmental legislation." | Legal /Technical | The TSOs believe that the existing drafting is appropriate.
4 | Payment | Clause 4.1.1 &Clause 4.2.3 | Clause 4.1.1 - the Company should not be able to unilaterally amend the Charging Statement and Payment Rates - these should be subject to public consultation Clause 4.2.3 - This should be reciprocal. Both parties should be able to set off amounts due to the other party under this Agreement net of amounts due to it from the other Party under this Agreement or any other agreements. | Legal | These clauses are the same as the existing corresponding HAS clauses. With regard to clause 4.1.1, the Company does not have the right to unilaterally amend the payment rates. They are subject to RA approval. With regard to clause 4.2.3, the TSOs disagaree with the suggestion to allow offset of amounts relative to other agreements.
5 | Monitoring and Metering | Clause 5.3
6 | Assignment | Clause 6.2 | References to "transmission system operator" should be capitalised as this is a defined term. | Legal | Yes, this has been amended accordingly.
7 | Variations | Clause 7.3 & 7.5 | Clause 7.3 - any chnages of this nature should be defined as a "Change in Law" and the Parties should be able to make such changes to the Agreement as are necessary. If the Parties cannot agree the proposed changes either party should be able to refer the matter to an Expert for determination (not the Regulatory Authority). Clause 7.3.1 - At the end of this sub-clause add the words "(incuding any reorganisation of the SEM)" Clause 7.5 - If the Parties cannot agree the proposed changes either party should be able to refer the matter to an Expert for determination (not the Regulatory Authority). | Legal | These clauses are the same as the corresponding clauses in the existing HAS contracts and the TSOs believe that there is no reason to re-draft them.
8 | Termination | Clause 8 | Clause 8.1 - Again the Term needs to be considered. The ability in Clause 8.1 of either Party to terminate by giving 3 months' notice is not appropriate for an intended 1 year term. Clause 8.2 (vii) - please see response to Consultation Question 4 Clause 8.3 - The circumstances by which the Service Provder can terminate the Agreement should mirror (in so far as is possible) the circumstances in which the Company can terminate the Agreement. For example, the Service Provider should be able to terminate the Agreement on (i) termination of the Trading and Settlement Code save where the same is replaced with alternative electricity trading arrangements; (ii) in relaton to the Company, wind up/dissolution of the Company, receiver, administrative receiver etc being appointed, any scheme of arrangements being entered into (other than for the purpose of a solvent reconstruction or amalgamation...), inability to pay its debts. | Legal | The TSOs believe that the termination clauses should remain as drafted. A more detailed explanation of this is given in the answer to Q4 in the consultation decision paper.
9 | Effect of Termination
10 | Force Majeure | Clause 10.2(a) | Notification of Force Majeure should be in writing. | Legal | The TSOs believe that writing is not the best means for notification of Force Majeure, as speed is of the essence and the most appropriate means at the time will be used. In, for example, the TSC the means of notification of Force Majeure is not specified.
11 | Limitation of Liability | Clause 11.1 & 11.2 | Suggested new sub-clause 11.1 (d) to be added as follows: "(in the case of breach by the Company) the loss of DS3 System Services Payments by the Service Provider under this Agreement, which, at the date of this Agreement, the Parties agree and acknowledge is reasonably foreseeable as likely to occur in the ordinary course of events from such breaches." Clause 11.2(a), after the words "loss of revenue" add, "(other than under this Agreement)" | Legal | These clauses are the same as the existing corresponding HAS clauses. The TSOs do not deem it appropriate to add additional liability clauses.
12 | Confidentiality | Clause 12.3.1 | AES requires the ability to share information with its Affiliates. This is due to the way in which AES is structured and the fact that employees who may be involved in this Agreement could be employed by another AES company that is not party to the Agreement and therefore need the ability to receive information. | Legal | Disclosure to Affilates is allowed in clause 12.3.1.
13 | Additional Costs | Clause 13.1 | The Company should not be able to set the Charging Statement and Payment Rates - these should be subject to public consultation. Any dispute over such payments should be determined by the Expert. | Legal | These clauses are the same as the existing corresponding HAS clauses. The Company does not have the right to unilaterally amend the payment rates. They are subject to RA approval.
14 | Dispute Resolution
15 | Miscellaneous | Clause 15.6 | At the end of the first sentence after "law", include the words "of the Jurisdiction". | Legal | This clause is the same as the existing corresponding HAS clause. The TSOs do not believe that it is necessary to amend it.
16 | Governing Law and Jurisdictions | Clause 16.3 | Any lawful finding of the Expert under the Agreement should also be conclusive and binding upon the parties. | Legal | This is provided for in Schedule 6 Section 3(b) of the SONI framework agreement and Schedule 6 Section 4(c) of the EirGrid framework agreement.
SCHEDULE 1 | Definitions |  | "Competent Authority" should also include the Commission for Energy Regulation, the SEM Committee, SEMO or any other successors of such bodies as may be in place from time to time. "Force Majeure" should not be limited to the events listed but should simply include (but not limit) those events. Unavailability of fuel, hydrogen or water (through no fault of the affected Party) should also be included in the list of FM events. | Legal | The definition of Competent Authority is the same as the existing corresponding HAS clauses. As this agreement is between the service provider and either SONI or EirGrid as appropriate, the relevant Regualtory Authority of the jurisdiction is included. The definition also covers the SEMC which is an "authority". The TSOs do not see a reason to include SEMO in this definition. The Force Majeure definition is the same as that in HAS. It is also similar to the TSC definition, although the TSC definition does not limit Force Majeure to include only listed events. The definition has been amended so that Force Majeure includes but is not limited to the listed events as per the TSC. This removes any need for an extra explicit clause.
SCHEDULE 2 | Operating Reserves
| Section 1 Operating Reserve Services |  | POR, SOR, TOR1, Scaling Factors include a combination of Product and Performance Scalars Product Scalars – now include a combination of reserve type scalar and reserve trigger scalar implemented in advance of any scalar design consultation decision. The proposed reserve trigger scalar amount calcualation methodology was not consulted on in the scalar design process. | Technical | This interim scalars were being consulted on as part of this consultation. The enduring scalars are separate. Please refer to Foreword of decision paper.
Section 2 Minimum Technical Requirements
| Section 3 Primary Operating Reserve (POR) - Available Volume, Payment and Performance Assessment |  | POR, SOR, TOR1, Scaling Factors include a combination of Product and Performance Scalars Product Scalars – now include a combination of reserve type scalar and reserve trigger scalar implemented in advance of any scalar design consultation decision. The proposed reserve trigger scalar amount calcualation methodology was not consulted on in the scalar design process. | Technical | This interim scalars were being consulted on as part of this consultation. The enduring scalars are separate. Please refer to Foreword of decision paper.
| Section 4 Secondary Operating Reserve (SOR) - Available Volume, Payment and Performance Assessment |  | POR, SOR, TOR1, Scaling Factors include a combination of Product and Performance Scalars Product Scalars – now include a combination of reserve type scalar and reserve trigger scalar implemented in advance of any scalar design consultation decision. The proposed reserve trigger scalar amount calcualation methodology was not consulted on in the scalar design process. | Technical | This interim scalars were being consulted on as part of this consultation. The enduring scalars are separate. Please refer to Foreword of decision paper.
| Section 5 Tertiary 1 Operating Reserve (TOR1) - Available Volume, Payment and Performance Assessment |  | POR, SOR, TOR1, Scaling Factors include a combination of Product and Performance Scalars Product Scalars – now include a combination of reserve type scalar and reserve trigger scalar implemented in advance of any scalar design consultation decision. The proposed reserve trigger scalar amount calcualation methodology was not consulted on in the scalar design process. | Technical | This interim scalars were being consulted on as part of this consultation. The enduring scalars are separate. Please refer to Foreword of decision paper.
Section 6 Tertiary 2 Operating Reserve (TOR2) - Available Volume, Payment and Performance Assessment
Section 7 Replacement Reserve - Available Volume, Payment and Performance Assessment
SCHEDULE 3 | Steady-State Reactive Power
Section 1 Provision of Service
Section 2 Minimum Technical Requirements
Section 3 Steady-State Reactive Power - Available Volume, Payment and Performance Assessment
SCHEDULE 4 | Other Services
SCHEDULE 4 - Part A | Section 1 Definition of Service
Section 2 Minimum Technical Requirements
Section 3 Synchronous Inertial Response - Available Volume and Payment
SCHEDULE 4 - Part B | Section 1 Definition of Service |  | SIR - The SIR Factor minimum value of 15 has been set at a level that rules out most at AES main units from receiving revenue from this product. AES views that the minimum level should be lower to ensure that all substantial conventional generation is remunerated for the provision of inertia when running. In the design of the product no reason or evidence was provided as to why an arbitrary minimum figure of 15 was implemented. | Technical | This is specified in SEM decision SEM-13-098 and has been consulted on twice. Further detail is given in 4.7.4 of the decision paper.
Section 2 Minimum Technical Requirements
| Section 3 Fast Frequency Response - Available Volume, Payment and Performance Assessment |  | SIR - The SIR Factor minimum value of 15 has been set at a level that rules out most at AES main units from receiving revenue from this product. AES views that the minimum level should be lower to ensure that all substantial conventional generation is remunerated for the provision of inertia when running. In the design of the product no reason or evidence was provided as to why an arbitrary minimum figure of 15 was implemented. | Technical | Duplicate comment.
SCHEDULE 4 - Part C | Section 1 Definition of Service
Section 2 Minimum Technical Requirements
| Section 3 Fast Post-Fault Active Power Recovery - Available Volume, Payment and Performance Assessment |  | FPAAPR available volume is defined as the product of the average MW output exported by the unit and the average declared availability to provide FPFAPR for the trading period. This was previously defined as the MW capability of the unit and thus the definition have been changed. | Technical | The payment definition for the FPFAPR system service in the Framework Agreement is consistent with SEM Committee Decision SEM-14-108.
SCHEDULE 4 - Part D | Section 1 Definition of Service
Section 2 Minimum Technical Requirements
| Section 3 Ramping Margin 1 (RM1) – Available Volume, Payment and Performance Assessment |  | Ramping – AES views that the use of Fail to synch is an inappropriate mechanism to monitor ramoping performance. Fail synch is a poor proxy for ramping performance and fails to capture ramping performance when synchronised | Technical | Please refer to decision paper section 4.6.6
| Section 4 Ramping Margin 3 (RM3) – Available Volume, Payment and Performance Assessment |  | Ramping – AES views that the use of Fail to synch is an inappropriate mechanism to monitor ramoping performance. Fail synch is a poor proxy for ramping performance and fails to capture ramping performance when synchronised | Technical | Please refer to decision paper section 4.6.6
| Section 5 Ramping Margin 8 (RM8) - Available Volume, Payment and Performance Assessment |  | Ramping – AES views that the use of Fail to synch is an inappropriate mechanism to monitor ramoping performance. Fail synch is a poor proxy for ramping performance and fails to capture ramping performance when synchronised | Technical | Please refer to decision paper section 4.6.6
SCHEDULE 4 - Part E | Section 1 Definition of Service
Section 2 Minimum Technical Requirements
Section 3 Dynamic Reactive Response (DRR) - Available Volume, Payment and Performance Assessment
SCHEDULE 5 | Billing and Payment Plan |  | Currently in Northern Ireland system services confirmation statements are issued daily on a D+3 basis to account for weekends and settled on a monthly time frame. The proposed new time line for DS3 System Services is for statement of charges (payments) to be issued after 25 business days (max) following the end of each charging period and allows 10 days for the provider to produce an invoice which has to then be paid within 10 business days after that. AES views this as an inferior solution relative to the current arrangements. In an energy market moving to shorter settlement periods we see benefit in aligning the system services settlement with the energy market time lines. The daily confirmation statements should be kept and the statements of charges produced on a weekly basis or at the latest in line with the energy market payment monthly timeframe. In short the current NI arrangements or better should be adopted. | Technical | Please refer to the answers to comments on Q9 in the decision paper.
SCHEDULE 6 | Dispute Resolution Procedure | Section 2 & Section 4 | Section 2 "Licence" is capitalised but not defined. "Electricity Arbitration Association" is defined as "EAA". Section 4 - the place of arbitration should be Northern Ireland? |  | The rules of the EAA define the place of arbitration to be England and Wales.
SCHEDULE 7 | Address Details and Billing Address
SCHEDULE 8 | Banking Details of the Service Provider
SCHEDULE 9 | Providing Unit and Operating Parameters