## Process
Template Signal List for the Provision of DS3 System Services
In order to comply with signalling requirements set out in the "DS3 System Services New Signalling Requirements" publication, a providing unit may be required to provide evidence of compliance in the form of a Wiring Certificate.
Any providing unit with requirements under the "DS3 System Services New Signalling Requirements" publication must request a site specific signal list from the TSO via e-mail to generator_testing@eirgrid.com or generator_testing@soni.ltd.uk.
The TSO shall issue a site specific signal list to the providing unit.
Upon completion of the necessary works, the providing unit shall submit a signed wiring certificate (using the 'Wiring Certificate' tab from the site specific signal list) verifying that all works have been carried out to make the relevant signals available to the TSO at the signalling interface. This will include physical wiring for sites communicating via RTU.

## Version Control
Signal List Version Control
Version | Date | Written by: | Reviewed by: | Approved by: | Description of changes | Change requested by
Note on D3: Administrator: All signal lists circulated to EMS and ESBT for Review before issuance.

## Signal List
Providing Unit Name | NI DSU / AGU Signal List - System Services - Reserve |  | V3.0 | 2019-03-14
Digital Output signals (from TSO) to Providing Unit |  | Permanent | 0.5 second pulse | 0.5 second pulse
|  | Common | Disable | Enable / ON
Signal Description | Digital - Control | Signal | Signal | Signal | Comment
Frequency Response Mode (Control) Disable | Control |  | 24 V DC |  | Control to TSO to disable OR service
Common |  | 0V DC
Frequency Response Mode (Control) Enable | Control |  |  | 24 V DC | Control to TSO to enable OR service
Reserve Response Mode 1 (Control) ON | Control |  |  | 24V DC | Command to activate Response mode 1
Reserve Response Mode 2 (Control) ON | Control |  |  | 24V DC | Command to activate Response mode 2
Reserve Response Mode 3 (Control) ON | Control |  |  | 24V DC | Command to activate Response mode 3
Reserve Response Mode 4 (Control) ON | Control |  |  | 24V DC | Command to activate Response mode 4
Reserve Response Mode 5 (Control) ON | Control |  |  | 24V DC | Command to activate Response mode 5
Digital Input Signals (to TSO) from Providing Unit |  | Permanent | 0.5 second pulse | 0.5 second pulse
|  | Common | Disable / OFF | Enable / ON
Signal Description | Digital - Feedback | Common | Signal | Signal | Comment
Frequency Response Mode (Feedback) Disabled | Feedback |  | 24 V DC |  | Feedback from IPP to confirm status of Frequency Response service
Common |  | 0V DC
Frequency Response Mode (Feedback) Enabled | Feedback |  |  | 24 V DC | Feedback from IPP to confirm status of Frequency Response service
Reserve Response Mode 1 (Feedback) OFF / ON | Feedback |  | 0 V DC | 24 V DC | Feedback from Providing Unit to confirm status of Mode 1
Reserve Response Mode 2 (Feedback) OFF / ON | Feedback |  | 0 V DC | 24 V DC | Feedback from Providing Unit to confirm status of Mode 2
Reserve Response Mode 3 (Feedback) OFF / ON | Feedback |  | 0 V DC | 24 V DC | Feedback from Providing Unit to confirm status of Mode 3
Reserve Response Mode 4 (Feedback) OFF / ON | Feedback |  | 0 V DC | 24 V DC | Feedback from Providing Unit to confirm status of Mode 4
Reserve Response Mode 5 (Feedback) OFF / ON | Feedback |  | 0 V DC | 24 V DC | Feedback from Providing Unit to confirm status of Mode 5
Analogue Input Signals (to TSO) from Providing Unit
Signal Description | Analogue Signal | Signal | Range |  | Comment
FFR Availability | Analogue Signal | 0 - 10 mA | 0-XX MW |  | Signal identifies in real-time the remaining aggregate MW of FFR.
POR Availability | Analogue Signal | 0 - 10 mA | 0-XX MW |  | Signal identifies in real-time the remaining aggregate MW of POR
SOR Availability | Analogue Signal | 0 - 10 mA | 0-XX MW |  | Signal identifies in real-time the remaining aggregate MW of SOR
TOR1 Availability | Analogue Signal | 0 - 10 mA | 0-XX MW |  | Signal identifies in real-time the remaining aggregate MW of TOR1
Frequency Response Provided | Analogue Signal | 0 - 10 mA | 0-XX MW |  | Signal identifies in real-time the MW response being provided for FFR, POR, SOR, TOR1 and TOR2
Aggregated Incomer Load for all Sites Providing Frequency Response | Analogue Signal | 0 - 10 mA | 0-XX MW |  | Signal identifies in real-time the aggregate MW load at the main incomers of the IDS providing FFR, POR, SOR, TOR1 and TOR2

## Wiring Certificate
Providing Unit Name | NI DSU / AGU Signal List - System Services - Reserve |  | V3.0 | 2019-03-14
Digital Output signals (from TSO) to Providing Unit |  | Permanent | 0.5 second pulse | 0.5 second pulse
|  | Common | Open | Close
Signal Description | Digital - Control | Signal | Signal | Signal | Signal in place | Functionality Confirmed
Frequency Response Mode (Control) Disable | Control |  | 24 V DC
Common |  | 0V DC
Frequency Response Mode (Control) Enable | Control |  |  | 24 V DC
Reserve Response Mode 1 (Control) ON | Control |  |  | 24V DC
Reserve Response Mode 2 (Control) ON | Control |  |  | 24V DC
Reserve Response Mode 3 (Control) ON | Control |  |  | 24V DC
Reserve Response Mode 4 (Control) ON | Control |  |  | 24V DC
Reserve Response Mode 5 (Control) ON | Control |  |  | 24V DC
Digital Input Signals (to TSO) from Providing Unit |  | Permanent | 0.5 second pulse | 0.5 second pulse
|  | Common | Disable / OFF | Enable / ON
Signal Description | Digital - Feedback | Common | Signal | Signal | Signal in place | Functionality Confirmed
Frequency Response Mode (Feedback) Disabled | Feedback |  | 24 V DC
Common |  | 0V DC
Frequency Response Mode (Feedback) Enabled | Feedback |  |  | 24 V DC
Reserve Response Mode 1 (Feedback) OFF / ON | Feedback |  | 0 V DC | 24 V DC
Reserve Response Mode 2 (Feedback) OFF / ON | Feedback |  | 0 V DC | 24 V DC
Reserve Response Mode 3 (Feedback) OFF / ON | Feedback |  | 0 V DC | 24 V DC
Reserve Response Mode 4 (Feedback) OFF / ON | Feedback |  | 0 V DC | 24 V DC
Reserve Response Mode 5 (Feedback) OFF / ON | Feedback |  | 0 V DC | 24 V DC
Analogue Input Signals (to TSO) from Providing Unit
Signal Description | Analogue Signal | Signal | Range |  | Signal in place | Functionality Confirmed
FFR Availability | Analogue Signal | 0 - 10 mA | 0-XX MW
POR Availability | Analogue Signal | 0 - 10 mA | 0-XX MW
SOR Availability | Analogue Signal | 0 - 10 mA | 0-XX MW
TOR1 Availability | Analogue Signal | 0 - 10 mA | 0-XX MW
Frequency Response Provided | Analogue Signal | 0 - 10 mA | 0-XX MW
Aggregated Incomer Load for all Sites Providing Frequency Response | Analogue Signal | 0 - 10 mA | 0-XX MW
Confirmation provided by: |  | Date: