## Cover Sheet
UNIT NAME Grid Code Compliance Progress Summary
Disclaimer:
This docuyment contains information (and/or attachments) which may be privileged or confidential. All content is intended solely for the use of the individual or entity to whom it is addressed. If you are not the intended recipient please be aware that any disclosure, copying, distribution or use of the contents of this document is prohibited. If you suspect that you have received this document in error please notify EirGrid immediately. Further information can be found at: http://www.eirgridgroup.com/legal/

## Version Control
Version Control
Version | Date | Written by: | Reviewed by: | Approved by: | Description of changes | Change requested by

## Scope of Works
Scope of Works
Outline the scope of the works required e.g.
New Unit
or
Governor refurbishment
MV switch gear replacement
etc.

## Progress Summary
XX1 Status XXth XXXXX 20XX
|  | %Test procedures agreed | % Performed on Primary Fuel | % Performed on Secondary Fuel | % Closed
| Phase A - Technical Data & Parameters |  |  |  | 0%
| Phase B - Offload tests | 0% |  |  | 0%
| Phase C - Onload tests | 0% | 0% | 0% | 0%
| Phase D - System Tests | 0% | 0% |  | 0%
| Update provided | Backfeed of Connection Transformer | Synchronisation of Unit (first export) | Start of High Export | Operational Certification
Current schedule
N-1 schedule
N-2 scheulde
Phase A | Description | Test Status
1 | Provision of Requirements | Open
2 | Provision of Studies & Model | Open
3 | Modes of Operation | Open
4 | Protection Settings | Open
5 | Governor Data | Open
6 | Excitation System & Generator | Open
7 | Transformer | Open
8 | Transformer Oil Test | Open
9 | Interface Cabling Scheme | Open
10 | Earthing & Lightning Protection | Open
11 | Power Station CT's & VT's | Open
12 | Function and accuracy check of protection | Open
13 | Operation & Interlocking Check | Open
14 | Interface Cabling Checks | Open
15 | Metering Equipment | Open
16 | Insulation resistance tests | Open
17 | Resistance test for connections. | Open
18 | Authorisation to Construct | Open
19 | Unit Registration | Open
20 | Operational Information | Open
21 | Operation Instruction & Standard Operating Procedure | Open
22 | Declaration of Fitness | Open
23 | Energisation Instruction | Open
24 | Isolation for Energisation | Open
Phase B | Description | Test procedure agreed | Test Status Primary Fuel
25 | Energise transformer | Open | Open
26 | Insulation Resistance Tests | Open | Open
27 | Resistance test for connections. | Open | Open
28 | Function and accuracy check of protection | Open | Open
29 | Signal Interface | Open | Open
30 | Generator Excitation - offline checks | Open | Open
31 | Function Check of protection alarm | Open | Open
32 | Function check of signals | Open | Open
33 | Turbine overspeed test. | Open | Open
34 | Generator Governor - offline checks | Open | Open
35 | Synchroniser Checks | Open | Open
36 | Declarations of Fitness | Open | Open
Phase C | Description | Test procedure Agreed | Testing Completed on Primary Fuel | Testing Completed on Secondary Fuel | Test Status
37 | Synchronise generator. | Open | Open | Open | Open
38 | Block Load | Open | Open | Open | Open
39 | Governor response and Operating Reserves | Open | Open | Open | Open
40 | Governor Droop | Open | Open | Open | Open
41 | Governor Deadband | Open | Open | Open | Open
42 | Minimum Generation | Open | Open | Open | Open
43 | Ramp Rates | Open | Open | Open | Open
44 | Trip to House Load | Open | Open | Open | Open
45 | Startup Time | Open | Open | Open | Open
46 | Shutdown Time | Open | Open | Open | Open
47 | Operation on Primary/Secondary/Mix fuel | Open | Open | Open | Open
48 | Modes of Operation | Open | N/A | N/A | N/A
49 | Verification of Output vs Ambient Conditions | Open | Open | Open | Open
50 | Reactive Power Capability/Excitation Limiters | Open | Open | N/A | Open
51 | Automatic Voltage Regulator Droop | Open | Open | N/A | Open
52 | Online SCADA signals check | Open | N/A | Open | Open
53 | Generator capability over voltage range/rated PF | Open | Open | N/A | Open
54 | Operation at high and low frequency | Open | Open | Open | Open
55 | Alerts | Open | Open | N/A | Open
56 | Automatic Generator Control | Open | Open | N/A | Open
57 | Emergency power supplies | Open | Open | N/A | Open
58 | Auxillary/Balance of Plant Fault ride through | Open | Open | N/A | Open
59 | Online PSS and Excitation controller testing | Open | Open | N/A | Open
60 | Registered Capacity | Open | Open | Open | Open
61 | Registered Characteristics | Open | Open | Open | Open
62 | Reliability run | Open | Open | Open | Open
63 | Export Adjustment Factors | Open | Open | Open | Open
64 | Model Validation | Open | Open | Open | Open
65 | Technical Offer Data | N/A | Open | Open | Open
66 | Special Protection Scheme Testing | Open | Open | N/A | Open
Phase D | Description | Test procedure Agreed | Testing Completed on Primary Fuel | Testing Completed on Secondary Fuel | Test Status
67 | Black Start | Open | Open | Open | Open
68 | Operating Reserves | Open | Open | Open | Open
69 | Ramping Margins | Open | Open | Open | Open
70 | Fast Post Fault Active Power Recovery & Dynamic Reactive Response | Open | Open | Open | Open
71 | Steady State Reactive Power | Open | Open | Open | Open
72 | Synchronous Inertial Response | Open | Open | Open | Open

## Issues Log
No. | Issue Description | Owner | Action | Decision | Status
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
The Issues Log shall be populated with any items that are identified outside of the prescribed tests, identified following the closure of a prescribed test, or during performance monitoring of the unit, prior to issuance of an Operational Certificate. All items in the Issues Log shall be closed prior to the issuance of an Operational Certificate.

## Phase A
Test # | Test | Grid Code Reference | EirGrid Witness | Description | Comment | Status
1 | Provision of Requirements |  | No | EirGrid shall provide the customer with: - RoCoF assessment pack with the MSS data. - FRT report template. - Harmonics pack - Signal List, based on SLD - Template for incident reports - Specification and process for system alerts - Specification for AGC |  | Open
2 | Provision of Studies & Model |  | No | The unit shall provide the following studies: - Power System Stabiliser study - Voltage Fault Ride Through study - Rate of Change of Frequency study - Harmonics study The unit shall provide: - Dynamic models as used in the studies above. - Full Laplace representation of the plant. The unit shall provide a study demonstrating that the transformer tap range is sufficient to allow provision of the full reactive power capability requirements over the full range of system voltages per CC.7.3.6.1 |  | Open
3 | Modes of Operation |  | No | Where relevant (e.g. combined cycle plant), the unit shall provide a description of different plant configurations (e.g. combustion turbine and steam turbine configurations). Note this will inform the testing required in Phase C. |  | Open
4 | Protection Settings | CC.10.9.1 CC.10.9.2 CC.7.3.1.1 a-h | No | The unit shall agree the following protection settings with EirGrid: - generator - generator transformer(s) - unit transformer(s) - balance of plant Generator transformer shall have differential and buchholz protection and the unit transformer shall have overcurrent (HV side preferable), differential and buchholz protection for first energisation |  | Open
5 | Governor Data |  | No | The unit shall provide the following for the Governor System: - design sheets - settings list - FAT results The unit shall provide conversion charts for plant output for variations with ambient conditions |  | Open
6 | Excitation System & Generator | CC 10 CC.7.3.1.1(g) | No | The unit shall provide the following for the Excitation System: - data sheets - settings list - FAT results The unit shall provide the Generator data sheets The unit shall demonstrate compliance with the reactive power capability as required by CC.7.3.6 at transmission system voltages within the ranges specified in CC.8.3.2 |  | Open
7 | Transformer | CC.7.2.5 | No | The unit shall provide the following for the Generator Transformer: - as built data sheet - legible photograph of transformer Name Plate Rating - FAT results of including transformer impedance data (positive and zero phase sequence) for top centre and bottom tap positions. The unit shall provide the following for the Unit Transformer: - as built data sheet - legible photograph of transformer Name Plate Rating - FAT results of including transformer impedance data (positive and zero phase sequence) for top centre and bottom tap positions. |  | Open
8 | Transformer Oil Test |  |  | The unit shall provide on-site oil test results (moisture content and gas breakdown) for the Generator Transformer and Station/Unit Transformer. | Test is carried out with the transformer on site Pass/Fail is required with test results or statement that results are acceptable to the customer. | Open
9 | Interface Cabling Scheme | CC 7.2.3 CC 12 | Yes | The unit shall submit the following for review: - Inter-tripping schemes, - Interlocking schemes - SCADA signal schemes Check that proposed interlocking for Power Station fits in with EirGrid specification. |  | Open
10 | Earthing & Lightning Protection | CC 7.2.1 CC 7.2.1.5 | No Yes | The unit shall provide an inspection report confirming Power Station earthing and lightning protection system is complete for transformers and generator. The unit shall provide an inspection report confirming connection between Power Station earth grid and Transmission Station earth grid is complete (this will include earth resistance measurements) |  | Open
11 | Power Station CT's & VT's | CC 10 | No | The unit shall provide FAT & SAT results for all CT's & VT's on: - Generator bus ducts - MV incomer - Generator transformer - Unit transformer Confirm CT’s & VT's are suitable for function and keep a record of as-built characteristic. |  | Open
12 | Function and accuracy check of protection | CC 10 | Yes | The unit shall provide SAT results and commissioning documentation for function and accuracy check of all protection for: - generator - generator transformer - unit transformer - balance of plant including secondary cabling, by secondary current and voltage injection. Except for functions that have to be tested with the generator running |  | Open
13 | Operation & Interlocking Check | CC 7.2.4 | Yes | Check operation and interlocking for: - HV CB - HV Disconnect - HV Earth Switch - Generator CB - Generator Disconnect - Generator CB Earth Switch - MV CB - MV Earth Switch EirGrid subcontract in co-operation with Power Station, for those items of plant which are installed at this stage. |  | Open
14 | Interface Cabling Checks | CC 10 CC 12 | Yes | The unit shall provide SAT and commissioning documentation for function check of all trip commands, signals and alarms: - from Transmission Station to Power Station - from Power Station to Transmission Station - Check of all signals to the units SCADA system. Test carried out in co-operation with EirGrid subcontract including actual tripping of HV CB by emergency trip pushbutton |  | Open
15 | Metering Equipment | CC 9 | Yes | Check, calibration and sealing of Transmission Station metering including signals to Power Station. ESB Networks (Metering Services) to provide DoF for revenue metering as part of Energisation Instruction. (No action on the unit for Non-Contestable builds) |  | Open
16 | Insulation resistance tests |  | Yes | The unit shall provide the SAT results for insulation resistance tests of: - generator transformer HV and LV sides - unit transformer HV and LV sides - all MV apparatus being energised Check that all plant to be energised is in a fit state to be energised by doing an insulation measurement test or HV test as appropriate. |  | Open
17 | Resistance test for connections. |  | No | The unit shall provide the SAT results for resistance tests of connections installed following completion of insulation tests. Verify that connections of flexibles will carry the full load current. May be a combination of torque on the bolts and measurement of the resistance of the connections. |  | Open
18 | Authorisation to Construct |  |  | e-mail licensing@cru.ie (cc to Generator_Testing@eirgrid.com) requesting confirmation of consented MW capacity |  | Open
19 | Unit Registration |  | No | The unit must be registered in the market before energistaion. In order to register in the market, the unit must: - submit a fully completed party accession pack - submit a fully completed particpant notification pack The unit must be registered in EDIL before energisation. - submit a completed EDIL registration form - carry out EDIL training Deadline: 60 days before energisation |  | Open
20 | Operational Information |  |  | Provide the following to EirGrid Customer Relations via e-mail to info@eirgrid.com - 24 hour contacts - Authorised Operators - Authorised DOF givers Note. Authorised Operators must be agreed and trained with ESBN for switching to take place. |  | Open
21 | Operation Instruction & Standard Operating Procedure | CC 10.3 | No | Agree Operating Instruction, including a check to see that the procedures can be safely followed. Written by EirGrid, agreed with ESBN and the unit. Suitable operating personnel are available with call-out procedure that is in line with EirGrid Operating Instruction. The unit shall provide the Standard Operating Procedure which covers the following scenarios: - tripping of generator - failure of protection - failure of power supplies etc. |  | Open
22 | Declaration of Fitness |  | N/A | The unit shall issue Declarations of Fitness as specified in the Energisation Instruction. |  | Open
23 | Energisation Instruction |  | Yes | Agree Energisation Instruction for 1st energisation of the connection point. Written by EirGrid, agreed with ESBN and the unit. |  | Open
24 | Isolation for Energisation | Safety Procedures | Yes | Check secondary side and neutral connection of generator and unit transformer is completed up to suitable isolating points and that secondary VT neutral point is connected and earthed. Check that suitable (lockable) earthing facilities are available for the equipment on the other side of the isolating points. Check access for visual check of earth switch and isolators |  | Open
All Phase A tests to be completed to achieve Energisation Operational Notification

## Phase B
Test # | Test | Grid Code Reference | EirGrid Witness | Description | Comment | Test procedure Agreed | Test Status
25 | Energise transformer |  | Yes | Energise the connection point per agreed Energisation Instruction |  | Open | Open
26 | Insulation Resistance Tests |  | No | The unit shall provide SAT results for insulation resistance tests of: - MV cables / IPBs / switchgear that was not tested in phase A - generator stator Check that all plant to be energised is in a fit state to be energised by doing an insulation measurement test or HV test as appropriate. |  | Open | Open
27 | Resistance test for connections. |  | No | The unit shall provide the SAT results for resistance tests of connections on IPB flexibles following installation and completion of insulation tests. Verify that connections of flexibles will carry the full load current. May be a combination of torque on the bolts and measurement of the resistance of the connections. |  | Open | Open
28 | Function and accuracy check of protection | CC 10 | No | The unit shall provide SAT results and commissioning documentation for function and accuracy check of all protection that was not tested in phase A. Including secondary cabling, by secondary current and voltage injection. Except for functions that have to be tested with the generator running |  | Open | Open
29 | Signal Interface | CC 7.2.3 & CC 10 & CC12 | Yes | Function check of all Transmission Station trip commands and signals and alarms/recording: - from Transmission Station to Power Station - from Power Station to Transmission Station - from interface/NCC to SCADA system. Check actual tripping of HV CB by emergency trip pushbutton Note that some or all of these tests may already have been completed in Phase A tests. |  | Open | Open
30 | Generator Excitation - offline checks |  | Yes | Open Circuit and Short Circuit testing Verification of Xd and Short Circuit Ratio. CC7.3.1.1 (j) states that the short circuit ration of each Generation Unit shall be in accordance with IEC 60034 Functional checks of Excitation control (e.g. AVR stationer and dynamic control checks at no load condition) |  | Open | Open
31 | Function Check of protection alarm |  | Yes | Function Check of protection alarm by primary voltage and current injection during open and short circuit tests. |  | Open | Open
32 | Function check of signals |  | Yes | Function check of signal transmitters by primary voltage and current injection during open and short circuit tests. |  | Open | Open
33 | Turbine overspeed test. |  | No | Demonstrate operation of all turbine overspeed protection. |  | Open | Open
34 | Generator Governor - offline checks |  | Yes | Testing of Governor system - Functional checks (governor stationer and dynamic control checks at no load condition) |  | Open | Open
35 | Synchroniser Checks | CC 7.3.3 & CC 7.3.4 | Yes | Testing of synchroniser - Generator CB and check contact closing time. Test protocols of factory tests to be available. Testing of synchroniser by backfeeding to generator to check VTs and then by testing pulses to blocked generator CB during dummy synchroniser tests using high speed recorder. CC7.3.4 The synchronising facilities in CC7.3.3 shall facilitate synchronising under (a) frequency between 48-52 Hz and voltage between 99 kV-123 kV. |  | Open | Open
36 | Declarations of Fitness | CC 7.3.3 & CC 7.3.4 | N/A | Power Station to issue Declaration of Fitness Market Registration is completed Load Profiles for export have been approved by the TSO and SEM |  | Open | Open
All Phase B tests to be completed to achieve Interim Operational Notification

## Phase C
Test # | Test | Grid Code Reference | EirGrid Witness | Description | Comment | Test procedure Agreed | Testing Completed on Primary Fuel | Testing Completed on Secondary Fuel | Test Status | Link to template procedure on website
37 | Synchronise generator. | CC 7.3.3 & CC 7.3.4 | Yes | First synchronisation of the generator according to agreed test procedure. Demonstrate successful synchronisation in all modes e.g.: - Manual Local - Auto Local - Auto Remote (via DCS) - Manual Remote (if available) |  | Open | Open | Open | Open
38 | Block Load | CC 7.3.1.1 | Yes | Measure initial exported MW following synchronisation, before the unit begins loading up. Applies for Cold, Warm and Hot starts. |  | Open | Open | Open | Open
39 | Governor response and Operating Reserves | CC 7.3.1.1 | Yes | Testing of POR, SOR and TOR by frequency injection at various loads. Testing of RoCoF capability. Testing by simulation of defined frequency excursions within frequency control software of all connected primary movers, being gas turbine(s) or steam turbine(s). Carried out at mimum and maximum loads. |  | Open | Open | Open | Open
40 | Governor Droop | CC 7.3.1.1 & OC 4.3.4 | Yes | Measurement of governor droop characteristic at various loads by simulation of frequency change on turbine governor. Normally measured as part of test 46 |  | Open | Open | Open | Open
41 | Governor Deadband | CC 7.3.1.1 & OC 4.3.4 | Yes | Measurement of governor deadband characteristic by simulation of a defined frequency change on the governor turbine. |  | Open | Open | Open | Open
42 | Minimum Generation | CC 7.3.1.1 | Yes | Demonstrate that MW output and process parameters (e.g. temperatures and vibration levels) remain stable during sustained operation at the defined minimum generation. The Minimum Load value will be determined using meter data. |  | Open | Open | Open | Open
43 | Ramp Rates | CC 7.3.1.1 | Yes | Demonstration of capability to ramp up and down between defined load points (rate of change to be Grid Code compliant). The generator should demonstrate stable operation at Registered Capacity for some period following ramp up. |  | Open | Open | Open | Open
44 | Trip to House Load | CC 7.3.2 | Yes | Load rejection test at 100% load and resynchronisation across HV CB after 1 hour operating at house load. The unit must remain running at normal frequency, feeding its own auxiliaries while completely disconnected from the grid for the 1 hour up to when resynchronisation takes place. Demonstrate that the process parameters (e.g. temperatures and vibration levels) remain stable during sustained operation at house load. |  | Open | Open | Open | Open
45 | Startup Time | CC 7.3.1.1 | Yes | Demonstration of: - time to synchronising from cold, warm and hot starts - time from synchronising to minimum load on cold, warm and hot starts and following turbine and boiler trips. |  | Open | Open | Open | Open
46 | Shutdown Time | CC 7.3.1.1 | No | 54a) Demonstration of shutdown time from Minimum Load. 54b) Demonstration of hot and warm cooling boundaries Note this not included in the published template. |  | Open | Open | Open | Open
47 | Operation on Primary/Secondary/Mix fuel |  | Yes | Where relevant, demonstration of operation on different primary fuels, or mixes of primary fuels. This includes demonstration of times and ability to change between fuels and between mixes |  | Open | Open | Open | Open
48 | Modes of Operation |  | Yes | Where relevant (e.g. combined cycle plant), demonstration of operation in different plant configurations (e.g combustion turbine and steam turbine configurations) |  | Open | N/A | N/A | N/A
49 | Verification of Output vs Ambient Conditions |  | No | The unit shall verify the conversion charts provided in phase A by converting plant output in the given ambient conditions to Registered Capacity (temperature and pressure as defined in the Grid Code) . |  | Open | Open | Open | Open
50 | Reactive Power Capability/Excitation Limiters | CC 7.3.1.1 & CC 7.3.6 | Yes | Demonstration of the stability of the unit at all MW/Mvar settings within the generator stability envelope at rated grid voltage. Measurement of the maximum leading/lagging reactive power capability at various loads and after thermal stabilisation of the generator. This shall also demonstrate the action of automatic limiters (OEL and UEL) to prevent the generator from operating outside its stability envelope. |  | Open | Open | N/A | Open
51 | Automatic Voltage Regulator Droop | CC 7.3.1.1 & CC 7.3.6 | Yes | Demonstration of voltage regulator droop characteristic in relation to grid voltage. Tested by comparing the voltage at the generator terminals before and after a tap change on the Grid Connected Transformer |  | Open | Open | N/A | Open
52 | Online SCADA signals check | CC 7.3.1.1 & CC 7.3.6 | Yes | Demonstration of accurate transmission of voltage, current and power signals and all SCADA signals. |  | Open | N/A | Open | Open
53 | Generator capability over voltage range/rated PF | CC 7.3.1.1 | Yes | Demonstration of generator MW capability at minimum and maximum generator voltages at rated power factor. | Title and description don’t describe the test very well | Open | Open | N/A | Open
54 | Operation at high and low frequency | CC 7.3.1.1 & CC 7.3.2 | Yes | Demonstration of operation of plant on house load at high frequency and low frequency limits of operation for 60 minutes. This test is normally carried out in conjunction with the load rejection test. | Where has the load rejection test gone?? Reactive Power capability should be checked in Phase A… and this should be to Grid Code (more onerous than IEC standard) and should account for over fluxing (V/F)… could be compliant with full F range and full V range but not high V with low F. | Open | Open | Open | Open
55 | Alerts | OC 9 | Yes | Demonstration of amber, red and blue alerts. |  | Open | Open | N/A | Open
56 | Automatic Generator Control | CC 7.3.1.1 | Yes | Demonstration of direct control from NCC in line with AGC specification provided in phase A and in line with the published test procedure template. |  | Open | Open | N/A | Open
57 | Emergency power supplies | CC 13.1 | Yes | Demonstration of capability of diesel generator to supply Power Station emergency loads Procedure for operation in this mode to be provided to EirGrid. This shall include demonstration of secure backup power supply to the associated transmission station, as applicable. |  | Open | Open | N/A | Open
58 | Auxillary/Balance of Plant Fault ride through | CC 7.3.1.1 | Yes | Demonstration of capability to withstand a voltage interruption of the auxiliary system of 0.150 sec. |  | Open | Open | N/A | Open
59 | Online PSS and Excitation controller testing |  | Yes | Demonstration of the PSS performance in response to step changes in AVR reference. This may also include operational switching on the power system. |  | Open | Open | N/A | Open
60 | Registered Capacity |  | Yes | Demonstrate stable operation at registered capacity for defined time period. This is the maximum sustained output where the unit can achieve all Grid Code requirements (ramping, min load, reactive power, etc.) and comply with emissions requirements. Registered Capacity will be determined using meter data. To be adjusted for temperature and pressure as specified in the Grid Code. |  | Open | Open | Open | Open
61 | Registered Characteristics |  | No | Provision of generator data following commissioning tests. See Planning Code Appendix of the Grid Code. Updated PC.A information and dynamic models & PSS Parameters/Study based on test report information |  | Open | Open | Open | Open
62 | Reliability run |  | Yes | EirGrid will review the unit’s reliability run. This will be agreed with PSC through submission of agreed profiles. Testing tariffs shall apply under this phase. Unit shall be operating in its final configuration following completion of tuning (governor, AVR, PSS, ramp rates, etc.). Unit shall have frequency response ON for the duration of the test. Unit shall evaluate temperatures, vibrations and emissions against allowable limits in the report. |  | Open | Open | Open | Open
63 | Export Adjustment Factors |  | Yes | Measurement of Adjustment Factors at various load levels to convert from generated MW to exported MW: - Fixed Load - Scalar Data is gathered during minimum load and Registered Capacity tests. |  | Open | Open | Open | Open
64 | Model Validation | Grid Code modification MPID239 | No | Validation of dynamic model provided in phase A vs actual performance during testing |  | Open | Open | Open | Open
65 | Technical Offer Data | N/A | No | Submission and Validation of Technical Offer Data via Market Participant Interface. |  | N/A | Open | Open | Open
66 | Special Protection Scheme Testing |  | Yes | Where required |  | Open | Open | N/A | Open

## Phase D
Test # | Test | Grid Code Reference | EirGrid Witness | Description | Comment | Test procedure Agreed | Testing Completed on Primary Fuel | Testing Completed on Secondary Fuel | Test Status | Link to template procedure on website
67 | Black Start | System Services |  | Demonstrate Black Start capability |  | Open | Open | Open | Open
68 | Operating Reserves | System Services |  | FFR, POR, SOR, TOR1, TOR2 Tested during Operating Reserve Tests Requires data recording at 20 ms resolution for FFR Unit must assess Inertia Credit the test report. |  | Open | Open | Open | Open
69 | Ramping Margins | System Services |  | Replacement Reserve Synchronised, RM1, RM3, RM8 are demonstrated during Ramp Rates test Replacement Reserve Desynchronised may be demonstrated during Hot/Warm/Cold start and ramp to full load |  | Open | Open | Open | Open
70 | Fast Post Fault Active Power Recovery & Dynamic Reactive Response | System Services |  | Tested through FRT studies |  | Open | Open | Open | Open
71 | Steady State Reactive Power | System Services |  | Demonstrated during Reactive Power Capability test |  | Open | Open | Open | Open
72 | Synchronous Inertial Response | System Services |  | Calculation based on unit Registered Characteristics |  | Open | Open | Open | Open

## Internal - Key Decisions
No. | Description/Query | Action/Decision | Status | Supporting documentation
1
2
3
4
5
6
7
8
9