## Cover Sheet
Signal List and Control System Parameter Settings for WINDFARM NAME (TLC) Type TSO XX MW v1.0
Disclaimer:
This Signal List contains information (and/or attachments) which may be privileged or confidential. All content is intended solely for the use of the individual or entity to whom it is addressed. If you are not the intended recipient please be aware that any disclosure, copying, distribution or use of the contents of this message is prohibited. If you suspect that you have received this Signal List in error please notify EirGrid immediately. Further information can be found at: http://www.eirgridgroup.com/legal/

## Version Control
WINDFARM NAME (TLC) Signal List Version Control
Version | Date | Written by: | Reviewed by: | Approved by: | Description of changes | Change requested by
1 |  |  |  |  | first draft
Note on D3: Administrator: All signal lists circulated to EMS and ESBT for Review before issuance.

## WFPS Required Inputs
WFPS Inputs for Signal List Development
1 | Wind Farm Power Station (WFPS) Name (including alternative names) | Included in submission 
2 | WFPS Maximum Export Capacity | Included in submission 
3 | WFPS Installed Capacity (for Phase developments, i.e. MEC 20MW Phase 1 10MWQ1 2014, Phase 2 additional 10MW Q2 2015 ) | Included in submission 
4 | The number of Market Units at the WFPS (Phase 1 &2 is one market unit or two separate market units, noting that if the WFPS consists of two market units then additional signals will be required). | Included in submission 
5 | Energisation Date | Included in submission 
6 | Single Line Diagram (Note that for changes in SLD's, the Signal list requirements may change) | Included in submission 
| · Revision Number | Included in submission 
| · Ownership boundaries | Included in submission 
| · HV CB positions (WFPS and ESBN as applicable) | Included in submission 
| · MV CB positions | Included in submission 
| · MV Feeders | Included in submission 
7 | Grid Connected Transformer tap range | Included in submission 
8 | Number of Met Masts on site - (if WFPS ≥10MW) | Included in submission 
9 | Nearest 110kV Station - normal feeding arrangements for WFPS | Included in submission 
10 | System Services Provided | Fast Frequency Reponse:  Primary Operating Reserve:  Secondary Operating Reserve:  Tertiary Operating Reserve:  Steady State Reactive Power: 
Information to be submitted to generator_testing@eirgrid.com

## 0) Signal List
WINDFARM NAME (TLC) |  | Type | TSO | XX | MW | v1.0 |  | Signals List is based on this Single Line Diagram (SLD) as inserted.
|  | RfG Type | D
EirGrid Signals, Command & Control Specification
Signals List |  | Registered Capacity: XX MW |  |  | Installed Plant: XXX MW
ETIE Ref | Digital Input Signals (signals sent to EirGrid) |  |  |  |  | Provided by | TSO Pass-through to | Grid Code reference
| Double Point Status Indications | (each individual input identified separately for clarity) | [5 empty] | Note: Signals treated as 2-bit binary
Digital Input Signals from Sub Station to EirGrid
A1 | WINDFARM T121 WFPS 20 kV CB |  | open |  |  | WFPS | N/A | Grid Code Signals List #1 PPM 1.7.1
A2 | WINDFARM T121 WFPS 20 kV CB |  | closed |  |  | WFPS | N/A | Grid Code Signals List #1 PPM 1.7.1
A3 | WINDFARM Feeder 1 20 kV CB |  | open |  |  | WFPS | N/A | Grid Code Signals List #1 PPM 1.7.1
A4 | WINDFARM Feeder 1 20 kV CB |  | closed |  |  | WFPS | N/A | Grid Code Signals List #1 PPM 1.7.1 | Typical SLD for a wind farm connecting to the system through a 38/20 kV transformer
A5 | WINDFARM Feeder 2 20 kV CB |  | open |  |  | WFPS | N/A | Grid Code Signals List #1 PPM 1.7.1
A6 | WINDFARM Feeder 2 20 kV CB |  | closed |  |  | WFPS | N/A | Grid Code Signals List #1 PPM 1.7.1
A7 | WINDFARM Feeder 3 20 kV CB |  | open |  |  | WFPS | N/A | Grid Code Signals List #1 PPM 1.7.1
A8 | WINDFARM Feeder 3 20 kV CB |  | closed |  |  | WFPS | N/A | Grid Code Signals List #1 PPM 1.7.1
A9 | WINDFARM Feeder 4 20 kV CB |  | open |  |  | WFPS | N/A | Grid Code Signals List #1 PPM 1.7.1
A10 | WINDFARM Feeder 4 20 kV CB |  | closed |  |  | WFPS | N/A | Grid Code Signals List #1 PPM 1.7.1
A11 | WINDFARM Feeder 5 20 kV CB |  | open |  |  | WFPS | N/A | Grid Code Signals List #1 PPM 1.7.1
A12 | WINDFARM Feeder 5 20 kV CB |  | closed |  |  | WFPS | N/A | Grid Code Signals List #1 PPM 1.7.1
A13 | TSO Remote Control Enable Switch |  | off |  |  | WFPS | N/A | Grid Code Signals List #1 PPM 1.7.1
A14 | TSO Remote Control Enable Switch |  | on |  |  | WFPS | N/A | Grid Code Signals List #1 PPM 1.7.1
A15 | Black Start Shutdown Feedback |  | off |  |  | ESBN | N/A | Feedback provided from transmission station only
A16 | Black Start Shutdown Feedback |  | on |  |  | ESBN | N/A | Feedback provided from transmission station only
A17 | Reactive Device >5 Mvar 1 |  | off |  |  | WFPS | N/A | Grid Code Signals List #1 PPM 1.7.1
A18 | Reactive Device >5 Mvar 1 |  | on |  |  | WFPS | N/A | Grid Code Signals List #1 PPM 1.7.1
Digital Input Signals from WTG System to EirGrid
B1 | Active Power Control facility status (feedback) |  | off |  |  | WFPS | N/A | Grid Code Signals List #4 PPM 1.7.1.4
B2 | Active Power Control facility status (feedback) |  | on |  |  | WFPS | N/A | Grid Code Signals List #4 PPM 1.7.1.4
B3 | Frequency Response System Mode Status (feedback) |  | off |  |  | WFPS | N/A | Grid Code Signals List #4 PPM 1.7.1.4
B4 | Frequency Response System Mode Status (feedback) |  | on |  |  | WFPS | N/A | Grid Code Signals List #4 PPM 1.7.1.4
B5 | Frequency Response Curve (feedback) |  | Curve 1 |  |  | WFPS | N/A | Grid Code Signals List #4 PPM 1.7.1.4
B6 | Frequency Response Curve (feedback) |  | Curve 2 |  |  | WFPS | N/A | Grid Code Signals List #4 PPM 1.7.1.4
B7 | AVR (kV) Control facility status (feedback) |  | off |  |  | WFPS | N/A | Grid Code Signals List #1 PPM 1.7.1
B8 | AVR (kV) Control facility status (feedback) |  | on |  |  | WFPS | N/A | Grid Code Signals List #1 PPM 1.7.1
B9 | Q (Mvar) Control facility status (feedback) |  | off |  |  | WFPS | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
B10 | Q (Mvar) Control facility status (feedback) |  | on |  |  | WFPS | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
B11 | Power Factor (PF) Control facility status (feedback) |  | off |  |  | WFPS | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
B12 | Power Factor (PF) Control facility status (feedback) |  | on |  |  | WFPS | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
B13 | Emulated Inertia status (feedback) |  | off |  |  | WFPS | N/A | System service requirement
B14 | Emulated Inertia status (feedback) |  | on |  |  | WFPS | N/A | System service requirement
Recommended cable 15-pair, 15 x 2 x 0.6sqmm, Twisted-Pair (TP), stranded
ETIE Ref | Analogue Input Signals (to EirGrid) |  |  |  |  | Provided by | TSO Pass-through to | Grid Code reference
Analogue Input Signals from Sub Station to EirGrid
C1 | Active Power Output at LV side of Grid Connected Transformer | -10 to 0 to 10 | mA | #VALUE! | MW | WFPS | N/A | Grid Code Signals List #1 PPM 1.7.1 (125% of Registered Capacity)
C2 | Reactive Power at LV side of Grid Connected Transformer | -10 to 0 to 10 | mA | #VALUE! | Mvar | WFPS | N/A | Grid Code Signals List #1 PPM 1.7.1 (150% of Reactive Power at Registered Capacity)
C3 | Voltage at LV side of Grid Connected Transformer | 0-10 | mA | 0 - 132 | kV | WFPS | N/A | Grid Code Signals List #1 PPM 1.7.1 (125% of nominal connection voltage)
Analogue Input Signals from WTG System to EirGrid
D1 | Available Active Power | 0-10 | mA | #VALUE! | MW | WFPS | N/A | Grid Code Signals List #1 PPM 1.7.1 (125% of Registered Capacity) 1 Second Granularity required for System Services
D2 | Active Power Control Setpoint (feedback) | 0-10 | mA | #VALUE! | MW | WFPS | N/A | Grid Code Signals List #4 PPM 1.7.1.4 (125% of Registered Capacity)
D3 | Voltage Control Setpoint (feedback) | 0-10 | mA | 99 - 132 | kV | WFPS | N/A | Grid Code Signals List #1 PPM 1.7.1
D4 | Mvar (Q) Control Setpoint (feedback) | -10 to 0 to 10 | mA | #VALUE! | Mvar | WFPS | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
D5 | Power Factor (PF) Control Setpoint (feedback) | -10 to 0 to 10 | mA | +/- 90 | degrees | WFPS | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012. Phase angle will be sent by NCC to WFPS Controller.
D6 | Frequency Droop Setting (feedback) | 0-10 | mA | 0-14 | % | WFPS | N/A | Grid Code Modification MPID 227 Approved by CER 26/02/2013
D7 | Transformer Tap Position | 0-10 | mA | 1 to 21 | Tap | WFPS | N/A | Grid Code Signals List #5 PPM 1.7.1.5
Analogue WTG Availability
D8 | %WTG not generating due to high wind | 0-10 | mA | 0-110 | % | WFPS | N/A | Grid Code Signals List #3 PPM 1.7.1.3
D9 | %WTG not generating due to low wind | 0-10 | mA | 0-110 | % | WFPS | N/A | Grid Code Signals List #3 PPM 1.7.1.3
D10 | Wind Farm Availability | 0-10 | mA | 0-110 | % | WFPS | N/A | Grid Code Signals List #3 PPM 1.7.1.3
Met 1 (if Registered Capacity >= 10 MW)
D11 | Emulated Inertia FFR availability | 0-10 | mA | 0-XX | MW | WFPS | N/A | Provides a reading of the available MW of FFR from Emulated Inertia
D12 | Emulated Inertia POR availability | 0-10 | mA | 0-XX | MW | WFPS | N/A | Provides a reading of the available MW of POR from Emulated Inertia
D13 | Wind Speed 1 | 0-10 | mA | 0-70 | m/s | WFPS | N/A | Grid Code Signals List #6 PPM 1.7.1.6
D14 | Wind Direction 1 | 0-10 | mA | 0-360 | deg | WFPS | N/A | Grid Code Signals List #6 PPM 1.7.1.6 (0mA = 0deg (from the North), 2.5mA = 90deg (from the East), 5mA = 180deg (from the South),7.5mA = 270deg (from West)
D15 | Air Temperature 1 | 0-10 | mA | -40-70 | C | WFPS | N/A | Grid Code Signals List #6 PPM 1.7.1.6
D16 | Air Pressure 1 | 0-10 | mA | 735-1060 | mBar | WFPS | N/A | Grid Code Signals List #6 PPM 1.7.1.6
Met N (if Registered Capacity >= 10 MW)
D17 | Wind Speed N | 0-10 | mA | 0-70 | m/s | WFPS | N/A | Grid Code Signals List #6 PPM 1.7.1.6
D18 | Wind Direction N | 0-10 | mA | 0-360 | deg | WFPS | N/A | Grid Code Signals List #6 PPM 1.7.1.6
D19 | Air Temperature N | 0-10 | mA | -40-70 | C | WFPS | N/A | Grid Code Signals List #6 PPM 1.7.1.6
D20 | Air Pressure N | 0-10 | mA | 735-1060 | mBar | WFPS | N/A | Grid Code Signals List #6 PPM 1.7.1.6
Recommended cable 25-pair cable: 25 x 2 x 0.6sqmm TP, stranded, individually screened pairs. Screens to be terminated by WFPS.
ETIE Ref | Digital Output Signals (from EirGrid) |  |  |  |  | Provided to | TSO Pass-through to | Distribution Code reference
| Double Command Outputs | (each individual relay output identified separately)
Digital Output Signals from EirGrid to WTG System
E1 | Active Power Control facility status |  | off | pulse | 0.5 seconds | WFPS | N/A | Grid Code Signals List #4 PPM 1.7.1.4
E2 | Active Power Control facility status |  | on | pulse | 0.5 seconds | WFPS | N/A | Grid Code Signals List #4 PPM 1.7.1.4
E3 | Frequency Response System Mode Status |  | off | pulse | 0.5 seconds | WFPS | N/A | Grid Code Signals List #5 PPM 1.7.1.5
E4 | Frequency Response System Mode Status |  | on | pulse | 0.5 seconds | WFPS | N/A | Grid Code Signals List #5 PPM 1.7.1.5
E5 | Frequency Response Curve Select |  | Curve 1 | pulse | 0.5 seconds | WFPS | N/A | Grid Code Signals List #5 PPM 1.7.1.5
E6 | Frequency Response Curve Select |  | Curve 2 | pulse | 0.5 seconds | WFPS | N/A | Grid Code Signals List #5 PPM 1.7.1.5
E7 | Emulated Intertia |  | off | pulse | 0.5 seconds | WFPS | N/A | Control from NCC to enable emulated inertia service
E8 | Emulated Intertia |  | on | pulse | 0.5 seconds | WFPS | N/A | Control from NCC to disable emulated inertia service
Digital Output Signals from EirGrid to Sub Station
F1 | Blackstart Shutdown |  | off | pulse | 0.5 seconds | WFPS | N/A | Connection CB Trip/ Inhibit function. N.B. this can be wired from the mimic panel, through the interface cabinet instead of via ETIE.
F2 | Blackstart Shutdown |  | on | pulse | 0.5 seconds | WFPS | N/A | Connection CB Trip/ Inhibit function. N.B. this can be wired from the mimic panel, through the interface cabinet instead of via ETIE.
Strobe Enable Pulse
Digital Output Signals from EirGrid to WTG System
E9 | Digital Output Active Power Control Setpoint Enable |  |  | pulse | 0.5 seconds | WFPS | N/A | Grid Code Signals List #4 PPM 1.7.1.4
E10 | Digital Output Voltage Control (kV) Setpoint Enable |  |  | pulse | 0.5 seconds | WFPS | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
E11 | Digital Output Mvar Control (Q) Setpoint Enable |  |  | pulse | 0.5 seconds | WFPS | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
E12 | Digital Output Power Factor Control (PF) Setpoint Enable |  |  | pulse | 0.5 seconds | WFPS | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
E13 | Digital Output Frequency Droop Setting Enable |  |  | pulse | 0.5 seconds | WFPS | N/A | Grid Code Modification MPID 227 Approved by CER 26/02/2013
Single Command Outputs
E14 | Voltage Control facility status ON |  | on | pulse | 0.5 seconds | WFPS | N/A | Grid Code Signals List #1 PPM 1.7.1
E15 | Mvar (Q) Control Facility status ON |  | on | pulse | 0.5 seconds | WFPS | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
E16 | Power Factor (PF) Control facility status ON |  | on | pulse | 0.5 seconds | WFPS | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
Recommended Cable 15-pair Screened Cable : 15 x 2 x 0.6sqmm, Twisted-Pair ( TP).
ETIE Ref | Analogue Output Signals (from EirGrid) |  |  |  |  | Provided to | TSO Pass-through to | Distribution Code reference
Analogue Output Signals from EirGrid to WTG System
G1 | Analogue Output Active Power Control Setpoint | 4 - 20 | mA | #VALUE! | MW | WFPS | N/A | Grid Code Signals List #4 PPM 1.7.1.4 (125% of Registered Capacity)
G2 | Analogue Voltage Control Setpoint | 4 - 20 | mA | 99 - 132 | kV | WFPS | N/A | Grid Code Signals List #1 PPM 1.7.1
G3 | Analogue Mvar (Q) Control Setpoint | 4 - 20 | mA | #VALUE! | Mvar | WFPS | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
G4 | Analogue Power Factor (PF) Control Setpoint | 4 - 20 | mA | +/- 90 | degrees | WFPS | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
G5 | Frequency Droop Setting | 4 - 20 | mA | 0-14 | % | WFPS | N/A | Grid Code Modification MPID 227 Approved by CER 26/02/2013
Recommended cable 5-pair cable: 5 x 2 x 0.6sqmm TP, stranded, individually screened pairs. Screens to be terminated by WFPS.
Note on D1: Administrator: Insert the Type of the Wind Farm
Note on E1: Administrator: Insert the Registered Capacity of the WFPS
Note on A6: EirGrid Telecoms Interface Enclosure
Note on H6: No IPP involvement unless otherwise confirmed
Note on B24: MacManus, Colm: BSSD Feedback is wired from Tx station mimic panel directly to RTU (not via ETIE) Ensure ETIE is marked up correctly In SCS stations: BSSD is implemented via SCS (not via RTU, not via ETIE).
Note on E50: +/-125%
Note on E52: 110kV: 0 to 132 kV 38kV: 0 to 45.6 kV 20kV: 0 to 24 kV
Note on E55: 0-125% 1 Second Granularity required for System Services
Note on E56: 0-125%
Note on E57: 110kV: 99 to 132 kV 38kV: 34.2 to 45.6 kV 20kV: 18 to 24 kV
Note on E61: Ensure tap range starts at 1: -13 to +13 should be 1 to 27 -13 to +7 should be 1 to 21
Note on B98: MacManus, Colm: BSSD command should be wired direct to RTU from Station Mimic Panel in all instances except in SCS type stations where we install a TSO RTU with integrated ETIE Ensure ETIE is marked up correctly
Note on E118: 0 to 125%

## 1a) Inst.Info & Contact Details
WINDFARM NAME (TLC) Information and Contact Details to be sent by WFPS via ESB Networks to EirGrid (generator_testing@EirGrid.com)
Information may be sent to by email: generator_testing@eirgrid.com, Fax: +353 (0)1 661 5375 or Post to: Operational Services & Performance, EirGrid, The Oval, 160 Shelbourne Road, Ballsbridge, Dublin 4
DATE
| HV SUB STATION NAME |  |  |  |  | ESBTS Team |  | Liam Boland
[6 empty] | Nessan Heaslip | Karl O'Keeffe | Noel Cowhey
| EirGrid Contact Person | Colm MacManus | PHONE: |  | (+353) 1 23 70168 | Robert Groarke | Oisín Goulding
| OSP Generic Email: Generator_testing@eirgrid.com |  |  |  |  | Frank Donnelly | Colm MacManus
| EMS Generic Email: ems.services@eirgrid.com |  |  |  |  | Liam Delany | C&T Team
[6 empty] | Niall Molloy | Ciarán Maguire
| ESBTS Project Manager | ESBTS Team | PHONE: |  | (+353) 1 7027835
| ESBTS Commissioner | ESBTS Team | PHONE: |  | (+353) 1 7027835
ESBTS Generic Email: esbts.scada.services@esb.ie
| ESB Networks (SPOC) |  | PHONE:
ESB Networks Build Generic Email: IPPdelivery@esb.ie
| ESB Networks (switchgear) |  | PHONE: |  | (+ )
| ESB Networks (metering) |  | PHONE: |  | (+ )
| WFPS Project Manager |  | PHONE: |  | (+ )
| Electrical Contractor |  | PHONE: |  | (+ )
| Turbine Contractor |  | PHONE: |  | (+ )
| Work Programme / Schedule (.mpp format) |  |  | Insert File
| Single Line Diagram |  |  | Insert file
| Site Layout Drawing on OS Map |  |  | Insert file
| Substation & Control Building Layout Drawing on OS Map |  |  | Insert file
| WFPS Energy Management System %error |  |  | %
| Directions including Map to the Wind Farm Power Station | Insert Map and brief description
| Safety & Site information | WFPS to provide details
ESBTS Standard Requirements from WFPS (may be customised for particular sites):
1) 90sq mm earth for Telecoms earth bar. 2) 35sq mm bonded from external earth grid to GPS clock antenna mounting bracket and if applicable Satellite antenna mounting bracket. 3) 48V DC Power System consisting of Switched Mode Power Supply (SMPS) with sealed cell battery. 4) If applicable - Fibre termination cabinet with fibre termination unit and fibre to distant station. 5) Satellite link consisting of Satellite transceiver and antenna if applicable. Satellite antenna preferably on a south facing wall with a clear view of the horizon. 6) Install and terminate process control and signal cables in ETI (the wiring schedule is available as a worksheet in the signal list excel file).
| ESB Telecom Services - Indicative Timelines for on site works | 1) 3 weeks notice required by ESBTS to schedule resources. 2) ~1 week to install the RTU cabinet with integrated ETI and GPS clock, GPS clock antenna. 3) ~1 week to pre commission the RTU referenced to frozen signal list with WFPS electrical and WTG contractors. 4) ~1 week to install and commission the satellite link including antenna (if applicable). 5) ~2 days to commission the fibre link (if applicable). 6) ~1 week to commission the RTU with WFPS electrical and WTG contractors.

## 1b) WFPS Wiring Completion Cert
WINDFARM NAME (TLC) |  | Type | TSO | XX | MW | v1.0 |  | Signals List is based on this Single Line Diagram (SLD) as inserted. | Wiring Completion Cert
|  | RfG Type | D
EirGrid Signals, Command & Control Specification | [8 empty] | Continuity Check Complete
WFPS Wiring Completion Certificate (to EirGrid ETIE/RTU) to be sent by WFPS to EirGrid (generator_testing@eirgrid.com)
ETIE Ref | Digital Input Signals (signals sent to EirGrid) |  |  |  |  | Provided by | TSO Pass-through to | Grid Code reference
| Double Point Status Indications | (each individual input identified separately for clarity)
Digital Input Signals from Sub Station to EirGrid
A1 | WINDFARM T121 WFPS 20 kV CB |  | open |  |  | WFPS | N/A | Grid Code Signals List #1 PPM 1.7.1
A2 | WINDFARM T121 WFPS 20 kV CB |  | closed |  |  | WFPS | N/A | Grid Code Signals List #1 PPM 1.7.1
A3 | WINDFARM Feeder 1 20 kV CB |  | open |  |  | WFPS | N/A | Grid Code Signals List #1 PPM 1.7.1
A4 | WINDFARM Feeder 1 20 kV CB |  | closed |  |  | WFPS | N/A | Grid Code Signals List #1 PPM 1.7.1
A5 | WINDFARM Feeder 2 20 kV CB |  | open |  |  | WFPS | N/A | Grid Code Signals List #1 PPM 1.7.1
A6 | WINDFARM Feeder 2 20 kV CB |  | closed |  |  | WFPS | N/A | Grid Code Signals List #1 PPM 1.7.1
A7 | WINDFARM Feeder 3 20 kV CB |  | open |  |  | WFPS | N/A | Grid Code Signals List #1 PPM 1.7.1
A8 | WINDFARM Feeder 3 20 kV CB |  | closed |  |  | WFPS | N/A | Grid Code Signals List #1 PPM 1.7.1
A9 | WINDFARM Feeder 4 20 kV CB |  | open |  |  | WFPS | N/A | Grid Code Signals List #1 PPM 1.7.1
A10 | WINDFARM Feeder 4 20 kV CB |  | closed |  |  | WFPS | N/A | Grid Code Signals List #1 PPM 1.7.1
A11 | WINDFARM Feeder 5 20 kV CB |  | open |  |  | WFPS | N/A | Grid Code Signals List #1 PPM 1.7.1
A12 | WINDFARM Feeder 5 20 kV CB |  | closed |  |  | WFPS | N/A | Grid Code Signals List #1 PPM 1.7.1
A13 | TSO Remote Control Enable Switch |  | off |  |  | WFPS | N/A | Grid Code Signals List #1 PPM 1.7.1
A14 | TSO Remote Control Enable Switch |  | on |  |  | WFPS | N/A | Grid Code Signals List #1 PPM 1.7.1
A15 | Black Start Shutdown Feedback |  | off |  |  | ESBN | N/A | Feedback provided from transmission station only
A16 | Black Start Shutdown Feedback |  | on |  |  | ESBN | N/A | Feedback provided from transmission station only
A17 | Reactive Device >5 Mvar 1 |  | off |  |  | WFPS | N/A | Grid Code Signals List #1 PPM 1.7.1
A18 | Reactive Device >5 Mvar 1 |  | on |  |  | WFPS | N/A | Grid Code Signals List #1 PPM 1.7.1
Digital Input Signals from WTG System to EirGrid
B1 | Active Power Control facility status (feedback) |  | off |  |  | WFPS | N/A | Grid Code Signals List #4 PPM 1.7.1.4
B2 | Active Power Control facility status (feedback) |  | on |  |  | WFPS | N/A | Grid Code Signals List #4 PPM 1.7.1.4
B3 | Frequency Response System Mode Status (feedback) |  | off |  |  | WFPS | N/A | Grid Code Signals List #4 PPM 1.7.1.4
B4 | Frequency Response System Mode Status (feedback) |  | on |  |  | WFPS | N/A | Grid Code Signals List #4 PPM 1.7.1.4
B5 | Frequency Response Curve (feedback) |  | Curve 1 |  |  | WFPS | N/A | Grid Code Signals List #4 PPM 1.7.1.4
B6 | Frequency Response Curve (feedback) |  | Curve 2 |  |  | WFPS | N/A | Grid Code Signals List #4 PPM 1.7.1.4
B7 | AVR (kV) Control facility status (feedback) |  | off |  |  | WFPS | N/A | Grid Code Signals List #1 PPM 1.7.1
B8 | AVR (kV) Control facility status (feedback) |  | on |  |  | WFPS | N/A | Grid Code Signals List #1 PPM 1.7.1
B9 | Q (Mvar) Control facility status (feedback) |  | off |  |  | WFPS | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
B10 | Q (Mvar) Control facility status (feedback) |  | on |  |  | WFPS | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
B11 | Power Factor (PF) Control facility status (feedback) |  | off |  |  | WFPS | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
B12 | Power Factor (PF) Control facility status (feedback) |  | on |  |  | WFPS | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
B13 | Emulated Inertia status (feedback) |  | off |  |  | WFPS | N/A | System service requirement
B14 | Emulated Inertia status (feedback) |  | on |  |  | WFPS | N/A | System service requirement
Recommended cable 15-pair, 15 x 2 x 0.6sqmm, Twisted-Pair (TP), stranded
ETIE Ref | Analogue Input Signals (to EirGrid) |  |  |  |  | Provided by | TSO Pass-through to | Grid Code reference
Analogue Input Signals from Sub Station to EirGrid
C1 | Active Power Output at LV side of Grid Connected Transformer | -10 to 0 to 10 | mA | #VALUE! | MW | WFPS | N/A | Grid Code Signals List #1 PPM 1.7.1 (125% of Registered Capacity)
C2 | Reactive Power at LV side of Grid Connected Transformer | -10 to 0 to 10 | mA | #VALUE! | Mvar | WFPS | N/A | Grid Code Signals List #1 PPM 1.7.1 (150% of Reactive Power at Registered Capacity)
C3 | Voltage at LV side of Grid Connected Transformer | 0-10 | mA | 0 - 132 | kV | WFPS | N/A | Grid Code Signals List #1 PPM 1.7.1 (125% of nominal connection voltage)
Analogue Input Signals from WTG System to EirGrid
D1 | Available Active Power | 0-10 | mA | #VALUE! | MW | WFPS | N/A | Grid Code Signals List #1 PPM 1.7.1 (125% of Registered Capacity) 1 Second Granularity required for System Services
D2 | Active Power Control Setpoint (feedback) | 0-10 | mA | #VALUE! | MW | WFPS | N/A | Grid Code Signals List #4 PPM 1.7.1.4 (125% of Registered Capacity)
D3 | Voltage Control Setpoint (feedback) | 0-10 | mA | 99 - 132 | kV | WFPS | N/A | Grid Code Signals List #1 PPM 1.7.1
D4 | Mvar (Q) Control Setpoint (feedback) | -10 to 0 to 10 | mA | #VALUE! | Mvar | WFPS | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
D5 | Power Factor (PF) Control Setpoint (feedback) | -10 to 0 to 10 | mA | +/- 90 | degrees | WFPS | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012. Phase angle will be sent by NCC to WFPS Controller.
D6 | Frequency Droop Setting (feedback) | 0-10 | mA | 0-14 | % | WFPS | N/A | Grid Code Modification MPID 227 Approved by CER 26/02/2013
D7 | Transformer Tap Position | 0-10 | mA | 1 to 21 | Tap | WFPS | N/A | Grid Code Signals List #5 PPM 1.7.1.5
Analogue WTG Availability
D8 | %WTG not generating due to high wind | 0-10 | mA | 0-110 | % | WFPS | N/A | Grid Code Signals List #3 PPM 1.7.1.3
D9 | %WTG not generating due to low wind | 0-10 | mA | 0-110 | % | WFPS | N/A | Grid Code Signals List #3 PPM 1.7.1.3
D10 | Wind Farm Availability | 0-10 | mA | 0-110 | % | WFPS | N/A | Grid Code Signals List #3 PPM 1.7.1.3
Met 1 (if Registered Capacity >= 10 MW)
D11 | Emulated Inertia FFR availability | 0-10 | mA | 0-XX | MW | WFPS | N/A | Provides a reading of the available MW of FFR from Emulated Inertia
D12 | Emulated Inertia POR availability | 0-10 | mA | 0-XX | MW | WFPS | N/A | Provides a reading of the available MW of POR from Emulated Inertia
D13 | Wind Speed 1 | 0-10 | mA | 0-70 | m/s | WFPS | N/A | Grid Code Signals List #6 PPM 1.7.1.6
D14 | Wind Direction 1 | 0-10 | mA | 0-360 | deg | WFPS | N/A | Grid Code Signals List #6 PPM 1.7.1.6 (0mA = 0deg (from the North), 2.5mA = 90deg (from the East), 5mA = 180deg (from the South),7.5mA = 270deg (from West)
D15 | Air Temperature 1 | 0-10 | mA | -40-70 | C | WFPS | N/A | Grid Code Signals List #6 PPM 1.7.1.6
D16 | Air Pressure 1 | 0-10 | mA | 735-1060 | mBar | WFPS | N/A | Grid Code Signals List #6 PPM 1.7.1.6
Met N (if Registered Capacity >= 10 MW)
D17 | Wind Speed N | 0-10 | mA | 0-70 | m/s | WFPS | N/A | Grid Code Signals List #6 PPM 1.7.1.6
D18 | Wind Direction N | 0-10 | mA | 0-360 | deg | WFPS | N/A | Grid Code Signals List #6 PPM 1.7.1.6
D19 | Air Temperature N | 0-10 | mA | -40-70 | C | WFPS | N/A | Grid Code Signals List #6 PPM 1.7.1.6
D20 | Air Pressure N | 0-10 | mA | 735-1060 | mBar | WFPS | N/A | Grid Code Signals List #6 PPM 1.7.1.6
Recommended cable 25-pair cable: 25 x 2 x 0.6sqmm TP, stranded, individually screened pairs. Screens to be terminated by WFPS.
ETIE Ref | Digital Output Signals (from EirGrid) |  |  |  |  | Provided to | TSO Pass-through to | Distribution Code reference
| Double Command Outputs | (each individual relay output identified separately)
Digital Output Signals from EirGrid to WTG System
E1 | Active Power Control facility status |  | off | pulse | 0.5 seconds | WFPS | N/A | Grid Code Signals List #4 PPM 1.7.1.4
E2 | Active Power Control facility status |  | on | pulse | 0.5 seconds | WFPS | N/A | Grid Code Signals List #4 PPM 1.7.1.4
E3 | Frequency Response System Mode Status |  | off | pulse | 0.5 seconds | WFPS | N/A | Grid Code Signals List #5 PPM 1.7.1.5
E4 | Frequency Response System Mode Status |  | on | pulse | 0.5 seconds | WFPS | N/A | Grid Code Signals List #5 PPM 1.7.1.5
E5 | Frequency Response Curve Select |  | Curve 1 | pulse | 0.5 seconds | WFPS | N/A | Grid Code Signals List #5 PPM 1.7.1.5
E6 | Frequency Response Curve Select |  | Curve 2 | pulse | 0.5 seconds | WFPS | N/A | Grid Code Signals List #5 PPM 1.7.1.5
E7 | Emulated Intertia |  | off | pulse | 0.5 seconds | WFPS | N/A | Control from NCC to enable emulated inertia service
E8 | Emulated Intertia |  | on | pulse | 0.5 seconds | WFPS | N/A | Control from NCC to disable emulated inertia service
Digital Output Signals from EirGrid to Sub Station
F1 | Blackstart Shutdown |  | off | pulse | 0.5 seconds | WFPS | N/A | Connection CB Trip/ Inhibit function. N.B. this can be wired from the mimic panel, through the interface cabinet instead of via ETIE.
F2 | Blackstart Shutdown |  | on | pulse | 0.5 seconds | WFPS | N/A | Connection CB Trip/ Inhibit function. N.B. this can be wired from the mimic panel, through the interface cabinet instead of via ETIE.
Strobe Enable Pulse
Digital Output Signals from EirGrid to WTG System
E9 | Digital Output Active Power Control Setpoint Enable |  |  | pulse | 0.5 seconds | WFPS | N/A | Grid Code Signals List #4 PPM 1.7.1.4
E10 | Digital Output Voltage Control (kV) Setpoint Enable |  |  | pulse | 0.5 seconds | WFPS | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
E11 | Digital Output Mvar Control (Q) Setpoint Enable |  |  | pulse | 0.5 seconds | WFPS | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
E12 | Digital Output Power Factor Control (PF) Setpoint Enable |  |  | pulse | 0.5 seconds | WFPS | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
E13 | Digital Output Frequency Droop Setting Enable |  |  | pulse | 0.5 seconds | WFPS | N/A | Grid Code Modification MPID 227 Approved by CER 26/02/2013
Single Command Outputs
E14 | Voltage Control facility status ON |  | on | pulse | 0.5 seconds | WFPS | N/A | Grid Code Signals List #1 PPM 1.7.1
E15 | Mvar (Q) Control Facility status ON |  | on | pulse | 0.5 seconds | WFPS | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
E16 | Power Factor (PF) Control facility status ON |  | on | pulse | 0.5 seconds | WFPS | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
Recommended Cable 15-pair Screened Cable : 15 x 2 x 0.6sqmm, Twisted-Pair ( TP).
ETIE Ref | Analogue Output Signals (from EirGrid) |  |  |  |  | Provided to | TSO Pass-through to | Distribution Code reference
Analogue Output Signals from EirGrid to WTG System
G1 | Analogue Output Active Power Control Setpoint | 4 - 20 | mA | #VALUE! | MW | WFPS | N/A | Grid Code Signals List #4 PPM 1.7.1.4 (125% of Registered Capacity)
G2 | Analogue Voltage Control Setpoint | 4 - 20 | mA | 99 - 132 | kV | WFPS | N/A | Grid Code Signals List #1 PPM 1.7.1
G3 | Analogue Mvar (Q) Control Setpoint | 4 - 20 | mA | #VALUE! | Mvar | WFPS | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
G4 | Analogue Power Factor (PF) Control Setpoint | 4 - 20 | mA | +/- 90 | degrees | WFPS | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
G5 | Frequency Droop Setting | 4 - 20 | mA | 0-14 | % | WFPS | N/A | Grid Code Modification MPID 227 Approved by CER 26/02/2013
Recommended cable 5-pair cable: 5 x 2 x 0.6sqmm TP, stranded, individually screened pairs. Screens to be terminated by WFPS.
All cables for interfacing at station interface cabinet or at EirGrid telecoms interface cabinet must be clearly marked with labels for identification. |  |  |  | Confirmed  |  |  |  | How are each of the MET signals generated? E.g. From a MET mast or WTGs
All cables for interfacing at station interface cabinet or EirGrid telecoms interface cabinet must be terminated at connection terminals (i.e. stripped, crimped and marked at terminal connections). |  |  |  | Confirmed  |  |  |  | Wind Speed: Wind Direction: Air Temperature: Air Pressure:
All cables for interfacing at station interface cabinet or EirGrid telecoms interface cabinet must use colour coding agreed by all parties i.e. ESBTS & WFPS. |  |  |  | Confirmed 
All analogue and digital interface signals must be tested and simulated for compliance with the frozen signal list agreed by all parties. |  |  |  | Confirmed 
ESBTS Satellite Dish bonded with 35 sq mm earth cable onto external station earth grid. |  |  |  | Confirmed 
ESBTS GPS clock antenna bonded with 35 sq mm earth cable onto external station earth grid. |  |  |  | Confirmed 
Information may be sent to by email: generator_testing@eirgrid.com, Fax: +353 (0)1 661 5375 or Post to: Operational Services & Performance, EirGrid, The Oval, 160 Shelbourne Road, Ballsbridge, Dublin 4 | [6 empty] | WFPS Name / Position | 0
WFPS Signature
Date
Note on A4: Administrator: To be completed by the IPP and sent to EirGrid to schedule ESBTS site attendance to perform continuity check
Note on A6: EirGrid Telecoms Interface Enclosure

## 2) ESB Telecoms Completion Cert
WINDFARM NAME (TLC) |  | Type | TSO | XX | MW | v1.0 |  | Completion Cert
|  | RfG Type | D
EirGrid Signals, Command & Control Specification | [7 empty] | Local SCADA Checks/Tests
ESB Telecoms Completion Cert to be sent by ESB Telecoms Services to EirGrid (generator_testing@eirgrid.com)
ETIE Ref | Digital Input Signals (signals sent to EirGrid) |  |  |  |  | Provided by | TSO Pass-through to
| Double Point Status Indications | (each individual input identified separately for clarity)
Digital Input Signals from Sub Station to EirGrid
A1 | WINDFARM T121 WFPS 20 kV CB |  | open |  |  | WFPS | N/A
A2 | WINDFARM T121 WFPS 20 kV CB |  | closed |  |  | WFPS | N/A
A3 | WINDFARM Feeder 1 20 kV CB |  | open |  |  | WFPS | N/A
A4 | WINDFARM Feeder 1 20 kV CB |  | closed |  |  | WFPS | N/A
A5 | WINDFARM Feeder 2 20 kV CB |  | open |  |  | WFPS | N/A
A6 | WINDFARM Feeder 2 20 kV CB |  | closed |  |  | WFPS | N/A
A7 | WINDFARM Feeder 3 20 kV CB |  | open |  |  | WFPS | N/A
A8 | WINDFARM Feeder 3 20 kV CB |  | closed |  |  | WFPS | N/A
A9 | WINDFARM Feeder 4 20 kV CB |  | open |  |  | WFPS | N/A
A10 | WINDFARM Feeder 4 20 kV CB |  | closed |  |  | WFPS | N/A
A11 | WINDFARM Feeder 5 20 kV CB |  | open |  |  | WFPS | N/A
A12 | WINDFARM Feeder 5 20 kV CB |  | closed |  |  | WFPS | N/A
A13 | TSO Remote Control Enable Switch |  | off |  |  | WFPS | N/A
A14 | TSO Remote Control Enable Switch |  | on |  |  | WFPS | N/A
A15 | Black Start Shutdown Feedback |  | off |  |  | ESBN | N/A
A16 | Black Start Shutdown Feedback |  | on |  |  | ESBN | N/A
A17 | Reactive Device >5 Mvar 1 |  | off |  |  | WFPS | N/A
A18 | Reactive Device >5 Mvar 1 |  | on |  |  | WFPS | N/A
Digital Input Signals from WTG System to EirGrid
B1 | Active Power Control facility status (feedback) |  | off |  |  | WFPS | N/A
B2 | Active Power Control facility status (feedback) |  | on |  |  | WFPS | N/A
B3 | Frequency Response System Mode Status (feedback) |  | off |  |  | WFPS | N/A
B4 | Frequency Response System Mode Status (feedback) |  | on |  |  | WFPS | N/A
B5 | Frequency Response Curve (feedback) |  | Curve 1 |  |  | WFPS | N/A
B6 | Frequency Response Curve (feedback) |  | Curve 2 |  |  | WFPS | N/A
B7 | AVR (kV) Control facility status (feedback) |  | off |  |  | WFPS | N/A
B8 | AVR (kV) Control facility status (feedback) |  | on |  |  | WFPS | N/A
B9 | Q (Mvar) Control facility status (feedback) |  | off |  |  | WFPS | N/A
B10 | Q (Mvar) Control facility status (feedback) |  | on |  |  | WFPS | N/A
B11 | Power Factor (PF) Control facility status (feedback) |  | off |  |  | WFPS | N/A
B12 | Power Factor (PF) Control facility status (feedback) |  | on |  |  | WFPS | N/A
B13 | Emulated Inertia status (feedback) |  | off |  |  | WFPS | N/A
B14 | Emulated Inertia status (feedback) |  | on |  |  | WFPS | N/A
Recommended cable 15-pair, 15 x 2 x 0.6sqmm, Twisted-Pair (TP), stranded
ETIE Ref | Analogue Input Signals (to EirGrid) |  |  |  |  | Provided by | TSO Pass-through to
Analogue Input Signals from Sub Station to EirGrid
C1 | Active Power Output at LV side of Grid Connected Transformer | -10 to 0 to 10 | mA | #VALUE! | MW | WFPS | N/A
C2 | Reactive Power at LV side of Grid Connected Transformer | -10 to 0 to 10 | mA | #VALUE! | Mvar | WFPS | N/A
C3 | Voltage at LV side of Grid Connected Transformer | 0-10 | mA | 0 - 132 | kV | WFPS | N/A
Analogue Input Signals from WTG System to EirGrid
D1 | Available Active Power | 0-10 | mA | #VALUE! | MW | WFPS | N/A
D2 | Active Power Control Setpoint (feedback) | 0-10 | mA | #VALUE! | MW | WFPS | N/A
D3 | Voltage Control Setpoint (feedback) | 0-10 | mA | 99 - 132 | kV | WFPS | N/A
D4 | Mvar (Q) Control Setpoint (feedback) | -10 to 0 to 10 | mA | #VALUE! | Mvar | WFPS | N/A
D5 | Power Factor (PF) Control Setpoint (feedback) | -10 to 0 to 10 | mA | +/- 90 | degrees | WFPS | N/A
D6 | Frequency Droop Setting (feedback) | 0-10 | mA | 0-14 | % | WFPS | N/A
D7 | Transformer Tap Position | 0-10 | mA | 1 to 21 | Tap | WFPS | N/A
Analogue WTG Availability
D8 | %WTG not generating due to high wind | 0-10 | mA | 0-110 | % | WFPS | N/A
D9 | %WTG not generating due to low wind | 0-10 | mA | 0-110 | % | WFPS | N/A
D10 | Wind Farm Availability | 0-10 | mA | 0-110 | % | WFPS | N/A
Met 1 (if Registered Capacity >= 10 MW)
D11 | Emulated Inertia FFR availability | 0-10 | mA | 0-XX | MW | WFPS | N/A
D12 | Emulated Inertia POR availability | 0-10 | mA | 0-XX | MW | WFPS | N/A
D13 | Wind Speed 1 | 0-10 | mA | 0-70 | m/s | WFPS | N/A
D14 | Wind Direction 1 | 0-10 | mA | 0-360 | deg | WFPS | N/A
D15 | Air Temperature 1 | 0-10 | mA | -40-70 | C | WFPS | N/A
D16 | Air Pressure 1 | 0-10 | mA | 735-1060 | mBar | WFPS | N/A
Met N (if Registered Capacity >= 10 MW)
D17 | Wind Speed N | 0-10 | mA | 0-70 | m/s | WFPS | N/A
D18 | Wind Direction N | 0-10 | mA | 0-360 | deg | WFPS | N/A
D19 | Air Temperature N | 0-10 | mA | -40-70 | C | WFPS | N/A
D20 | Air Pressure N | 0-10 | mA | 735-1060 | mBar | WFPS | N/A
Recommended cable 25-pair cable: 25 x 2 x 0.6sqmm TP, stranded, individually screened pairs. Screens to be terminated by WFPS.
ETIE Ref | Digital Output Signals (from EirGrid) |  |  |  |  | Provided to | TSO Pass-through to
| Double Command Outputs | (each individual relay output identified separately)
Digital Output Signals from EirGrid to WTG System
E1 | Active Power Control facility status |  | off | pulse | 0.5 seconds | WFPS | N/A
E2 | Active Power Control facility status |  | on | pulse | 0.5 seconds | WFPS | N/A
E3 | Frequency Response System Mode Status |  | off | pulse | 0.5 seconds | WFPS | N/A
E4 | Frequency Response System Mode Status |  | on | pulse | 0.5 seconds | WFPS | N/A
E5 | Frequency Response Curve Select |  | Curve 1 | pulse | 0.5 seconds | WFPS | N/A
E6 | Frequency Response Curve Select |  | Curve 2 | pulse | 0.5 seconds | WFPS | N/A
E7 | Emulated Intertia |  | off | pulse | 0.5 seconds | WFPS | N/A
E8 | Emulated Intertia |  | on | pulse | 0.5 seconds | WFPS | N/A
Digital Output Signals from EirGrid to Sub Station
F1 | Blackstart Shutdown |  | off | pulse | 0.5 seconds | WFPS | N/A
F2 | Blackstart Shutdown |  | on | pulse | 0.5 seconds | WFPS | N/A
Strobe Enable Pulse
Digital Output Signals from EirGrid to WTG System
E9 | Digital Output Active Power Control Setpoint Enable |  |  | pulse | 0.5 seconds | WFPS | N/A
E10 | Digital Output Voltage Control (kV) Setpoint Enable |  |  | pulse | 0.5 seconds | WFPS | N/A
E11 | Digital Output Mvar Control (Q) Setpoint Enable |  |  | pulse | 0.5 seconds | WFPS | N/A
E12 | Digital Output Power Factor Control (PF) Setpoint Enable |  |  | pulse | 0.5 seconds | WFPS | N/A
E13 | Digital Output Frequency Droop Setting Enable |  |  | pulse | 0.5 seconds | WFPS | N/A
Single Command Outputs
E14 | Voltage Control facility status ON |  | on | pulse | 0.5 seconds | WFPS | N/A
E15 | Mvar (Q) Control Facility status ON |  | on | pulse | 0.5 seconds | WFPS | N/A
E16 | Power Factor (PF) Control facility status ON |  | on | pulse | 0.5 seconds | WFPS | N/A
Recommended Cable 15-pair Screened Cable : 15 x 2 x 0.6sqmm, Twisted-Pair ( TP).
``
ETIE Ref | Analogue Output Signals (from EirGrid) |  |  |  |  | Provided to | TSO Pass-through to
Analogue Output Signals from EirGrid to WTG System
G1 | Analogue Output Active Power Control Setpoint | 4 - 20 | mA | #VALUE! | MW | WFPS | N/A
G2 | Analogue Voltage Control Setpoint | 4 - 20 | mA | 99 - 132 | kV | WFPS | N/A
G3 | Analogue Mvar (Q) Control Setpoint | 4 - 20 | mA | #VALUE! | Mvar | WFPS | N/A
G4 | Analogue Power Factor (PF) Control Setpoint | 4 - 20 | mA | +/- 90 | degrees | WFPS | N/A
G5 | Frequency Droop Setting | 4 - 20 | mA | 0-14 | % | WFPS | N/A
Recommended cable 5-pair cable: 5 x 2 x 0.6sqmm TP, stranded, individually screened pairs. Screens to be terminated by WFPS.
All cables for interfacing at station interface cabinet or at EirGrid telecoms interface cabinet are installed and correct. |  |  |  | Confirmed  |  |  | ESBTS Name / Position | ESBTS Team
ESBTS Signature
Date
| NOTE: Non operable WFPS signals will result in rescheduling for re-commissioning and require another Joint Signals Test Cert to be performed. |  | Information may be sent to by email: generator_testing@eirgrid.com, Fax: +353 (0)1 661 5375 or Post to: Operational Services & Performance, EirGrid, The Oval, 160 Shelbourne Road, Ballsbridge, Dublin 4
Note on A6: EirGrid Telecoms Interface Enclosure

## 2 a) EMS Database Setup Cert
WINDFARM NAME (TLC) |  | Type | TSO | XX | MW | v1.0
|  | RfG Type | D
EirGrid Signals, Command & Control Specification
Energy Management System (EMS) Database setup Certificate
Completion Cert
Continuity Check Complete
Generator Modelled
Lines Modelled
Station Modelled
Calculations Updated
RTU Modelled
Display Work Completed:
WF SLD
Station SLD
Station List
Windfarm List
Embedded Wind
Windfarm Control
Station Wind MW
Wind Overview
Windfarm Availability Data
Blue Alert Page
Windfarm Weather Data
DCC signals provided via ICCP
EMS Name
EMS Signature
Date
EirGrid Internal Document - no IPP requirements. For Information only
Note on A4: Administrator: DCC to be Informed

## 3)Pre Energ. Sign&Con Test Cert
WINDFARM NAME (TLC) |  | Type | TSO | XX | MW | v1.0 |  | Pre Energisation Signals and Controls Test
|  | RfG Type | D
EirGrid Signals, Command & Control Specification | [7 empty] | Simulated □/Real □ value tested | mA Range | Value Range | Comment
Pre Energisation Signals & Controls Certificate to be sent by ESBT to EirGrid (generator_testing@eirgrid.com)
ETIE Ref | Digital Input Signals (signals sent to EirGrid) |  |  |  |  | Provided by | TSO Pass-through to
| Double Point Status Indications | (each individual input identified separately for clarity)
Digital Input Signals from Sub Station to EirGrid
A1 | WINDFARM T121 WFPS 20 kV CB |  | open |  |  | WFPS | N/A | Real □
A2 | WINDFARM T121 WFPS 20 kV CB |  | closed |  |  | WFPS | N/A | Real □
A3 | WINDFARM Feeder 1 20 kV CB |  | open |  |  | WFPS | N/A | Real □
A4 | WINDFARM Feeder 1 20 kV CB |  | closed |  |  | WFPS | N/A | Real □
A5 | WINDFARM Feeder 2 20 kV CB |  | open |  |  | WFPS | N/A | Real □
A6 | WINDFARM Feeder 2 20 kV CB |  | closed |  |  | WFPS | N/A | Real □
A7 | WINDFARM Feeder 3 20 kV CB |  | open |  |  | WFPS | N/A | Real □
A8 | WINDFARM Feeder 3 20 kV CB |  | closed |  |  | WFPS | N/A | Real □
A9 | WINDFARM Feeder 4 20 kV CB |  | open |  |  | WFPS | N/A | Real □
A10 | WINDFARM Feeder 4 20 kV CB |  | closed |  |  | WFPS | N/A | Real □
A11 | WINDFARM Feeder 5 20 kV CB |  | open |  |  | WFPS | N/A | Real □
A12 | WINDFARM Feeder 5 20 kV CB |  | closed |  |  | WFPS | N/A | Real □
A13 | TSO Remote Control Enable Switch |  | off |  |  | WFPS | N/A | Real □
A14 | TSO Remote Control Enable Switch |  | on |  |  | WFPS | N/A | Real □
A15 | Black Start Shutdown Feedback |  | off |  |  | ESBN | N/A | Real □
A16 | Black Start Shutdown Feedback |  | on |  |  | ESBN | N/A | Real □
A17 | Reactive Device >5 Mvar 1 |  | off |  |  | WFPS | N/A | Real □
A18 | Reactive Device >5 Mvar 1 |  | on |  |  | WFPS | N/A | Real □
Digital Input Signals from WTG System to EirGrid
B1 | Active Power Control facility status (feedback) |  | off |  |  | WFPS | N/A | Simulated □
B2 | Active Power Control facility status (feedback) |  | on |  |  | WFPS | N/A | Simulated □
B3 | Frequency Response System Mode Status (feedback) |  | off |  |  | WFPS | N/A | Simulated □
B4 | Frequency Response System Mode Status (feedback) |  | on |  |  | WFPS | N/A | Simulated □
B5 | Frequency Response Curve (feedback) |  | Curve 1 |  |  | WFPS | N/A | Simulated □
B6 | Frequency Response Curve (feedback) |  | Curve 2 |  |  | WFPS | N/A | Simulated □
B7 | AVR (kV) Control facility status (feedback) |  | off |  |  | WFPS | N/A | Simulated □
B8 | AVR (kV) Control facility status (feedback) |  | on |  |  | WFPS | N/A | Simulated □
B9 | Q (Mvar) Control facility status (feedback) |  | off |  |  | WFPS | N/A | Simulated □
B10 | Q (Mvar) Control facility status (feedback) |  | on |  |  | WFPS | N/A | Simulated □
B11 | Power Factor (PF) Control facility status (feedback) |  | off |  |  | WFPS | N/A | Simulated □
B12 | Power Factor (PF) Control facility status (feedback) |  | on |  |  | WFPS | N/A | Simulated □
B13 | Emulated Inertia status (feedback) |  | off |  |  | WFPS | N/A | Simulated □
B14 | Emulated Inertia status (feedback) |  | on |  |  | WFPS | N/A | Simulated □
Recommended cable 15-pair, 15 x 2 x 0.6sqmm, Twisted-Pair (TP), stranded
ETIE Ref | Analogue Input Signals (to EirGrid) |  |  |  |  | Provided by | TSO Pass-through to
Analogue Input Signals from Sub Station to EirGrid
C1 | Active Power Output at LV side of Grid Connected Transformer | -10 to 0 to 10 | mA | #VALUE! | MW | WFPS | N/A | Real □
C2 | Reactive Power at LV side of Grid Connected Transformer | -10 to 0 to 10 | mA | #VALUE! | Mvar | WFPS | N/A | Real □
C3 | Voltage at LV side of Grid Connected Transformer | 0-10 | mA | 0 - 132 | kV | WFPS | N/A | Real □
Analogue Input Signals from WTG System to EirGrid
D1 | Available Active Power | 0-10 | mA | #VALUE! | MW | WFPS | N/A | Simulated □
D2 | Active Power Control Setpoint (feedback) | 0-10 | mA | #VALUE! | MW | WFPS | N/A | Simulated □
D3 | Voltage Control Setpoint (feedback) | 0-10 | mA | 99 - 132 | kV | WFPS | N/A | Simulated □
D4 | Mvar (Q) Control Setpoint (feedback) | -10 to 0 to 10 | mA | #VALUE! | Mvar | WFPS | N/A | Simulated □
D5 | Power Factor (PF) Control Setpoint (feedback) | -10 to 0 to 10 | mA | +/- 90 | degrees | WFPS | N/A | Simulated □
D6 | Frequency Droop Setting (feedback) | 0-10 | mA | 0-14 | % | WFPS | N/A | Simulated □
D7 | Transformer Tap Position | 0-10 | mA | 1 to 21 | Tap | WFPS | N/A | Simulated □
Analogue WTG Availability
D8 | %WTG not generating due to high wind | 0-10 | mA | 0-110 | % | WFPS | N/A | Simulated □
D9 | %WTG not generating due to low wind | 0-10 | mA | 0-110 | % | WFPS | N/A | Simulated □
D10 | Wind Farm Availability | 0-10 | mA | 0-110 | % | WFPS | N/A | Simulated □
Met 1 (if Registered Capacity >= 10 MW)
D11 | Emulated Inertia FFR availability | 0-10 | mA | 0-XX | MW | WFPS | N/A | Simulated □
D12 | Emulated Inertia POR availability | 0-10 | mA | 0-XX | MW | WFPS | N/A | Simulated □
D13 | Wind Speed 1 | 0-10 | mA | 0-70 | m/s | WFPS | N/A | Simulated □
D14 | Wind Direction 1 | 0-10 | mA | 0-360 | deg | WFPS | N/A | Simulated □
D15 | Air Temperature 1 | 0-10 | mA | -40-70 | C | WFPS | N/A | Simulated □
D16 | Air Pressure 1 | 0-10 | mA | 735-1060 | mBar | WFPS | N/A | Simulated □
Met N (if Registered Capacity >= 10 MW)
D17 | Wind Speed N | 0-10 | mA | 0-70 | m/s | WFPS | N/A | Simulated □
D18 | Wind Direction N | 0-10 | mA | 0-360 | deg | WFPS | N/A | Simulated □
D19 | Air Temperature N | 0-10 | mA | -40-70 | C | WFPS | N/A | Simulated □
D20 | Air Pressure N | 0-10 | mA | 735-1060 | mBar | WFPS | N/A | Simulated □
Recommended cable 25-pair cable: 25 x 2 x 0.6sqmm TP, stranded, individually screened pairs. Screens to be terminated by WFPS.
ETIE Ref | Digital Output Signals (from EirGrid) |  |  |  |  | Provided to | TSO Pass-through to
| Double Command Outputs | (each individual relay output identified separately)
Digital Output Signals from EirGrid to WTG System
E1 | Active Power Control facility status |  | off | pulse | 0.5 seconds | WFPS | N/A | Simulated □
E2 | Active Power Control facility status |  | on | pulse | 0.5 seconds | WFPS | N/A | Simulated □
E3 | Frequency Response System Mode Status |  | off | pulse | 0.5 seconds | WFPS | N/A | Simulated □
E4 | Frequency Response System Mode Status |  | on | pulse | 0.5 seconds | WFPS | N/A | Simulated □
E5 | Frequency Response Curve Select |  | Curve 1 | pulse | 0.5 seconds | WFPS | N/A | Simulated □
E6 | Frequency Response Curve Select |  | Curve 2 | pulse | 0.5 seconds | WFPS | N/A | Simulated □
E7 | Emulated Intertia |  | off | pulse | 0.5 seconds | WFPS | N/A | Simulated □
E8 | Emulated Intertia |  | on | pulse | 0.5 seconds | WFPS | N/A | Simulated □
Digital Output Signals from EirGrid to Sub Station
F1 | Blackstart Shutdown |  | off | pulse | 0.5 seconds | WFPS | N/A | Real □
F2 | Blackstart Shutdown |  | on | pulse | 0.5 seconds | WFPS | N/A | Real □
Strobe Enable Pulse
Digital Output Signals from EirGrid to WTG System
E9 | Digital Output Active Power Control Setpoint Enable |  |  | pulse | 0.5 seconds | WFPS | N/A | Simulated □
E10 | Digital Output Voltage Control (kV) Setpoint Enable |  |  | pulse | 0.5 seconds | WFPS | N/A | Simulated □
E11 | Digital Output Mvar Control (Q) Setpoint Enable |  |  | pulse | 0.5 seconds | WFPS | N/A | Simulated □
E12 | Digital Output Power Factor Control (PF) Setpoint Enable |  |  | pulse | 0.5 seconds | WFPS | N/A | Simulated □
E13 | Digital Output Frequency Droop Setting Enable |  |  | pulse | 0.5 seconds | WFPS | N/A | Simulated □
Single Command Outputs
E14 | Voltage Control facility status ON |  | on | pulse | 0.5 seconds | WFPS | N/A | Simulated □
E15 | Mvar (Q) Control Facility status ON |  | on | pulse | 0.5 seconds | WFPS | N/A | Simulated □
E16 | Power Factor (PF) Control facility status ON |  | on | pulse | 0.5 seconds | WFPS | N/A | Simulated □
Recommended Cable 15-pair Screened Cable : 15 x 2 x 0.6sqmm, Twisted-Pair ( TP).
ETIE Ref | Analogue Output Signals (from EirGrid) |  |  |  |  | Provided to | TSO Pass-through to
Analogue Output Signals from EirGrid to WTG System
G1 | Analogue Output Active Power Control Setpoint | 4 - 20 | mA | #VALUE! | MW | WFPS | N/A | Simulated □
G2 | Analogue Voltage Control Setpoint | 4 - 20 | mA | 99 - 132 | kV | WFPS | N/A | Simulated □
G3 | Analogue Mvar (Q) Control Setpoint | 4 - 20 | mA | #VALUE! | Mvar | WFPS | N/A | Simulated □
G4 | Analogue Power Factor (PF) Control Setpoint | 4 - 20 | mA | +/- 90 | degrees | WFPS | N/A | Simulated □
G5 | Frequency Droop Setting | 4 - 20 | mA | 0-14 | % | WFPS | N/A | Simulated □
Recommended cable 5-pair cable: 5 x 2 x 0.6sqmm TP, stranded, individually screened pairs. Screens to be terminated by WFPS.
Simulation Point
Simulation Method
[6 empty] | WFPS Name / Position |  | 0
WFPS Signature
EMS Name
EMS Signature
| NOTE: Non operable WFPS signals will result in rescheduling for re-commissioning and require another Joint Signals Test Cert to be performed. |  |  |  |  | ESB Telecoms Name / Position |  | ESBTS Team
| Information may be sent to by email: generator_testing@eirgrid.com, Fax: +353 (0)1 661 5375 or Post to: System Support, EirGrid, The Oval, 160 Shelbourne Road, Ballsbridge, Dublin 4 |  |  |  |  | ESB Telecoms Signature
Date
Note on I1: Administrator: ESBTS Commission from NCC control desk to / via ETI to IPP plant.
Note on I3: Administrator: the electrical characteristics of IPP signals not tested due to plant unavailability must be simulated by IPP.
Note on A6: EirGrid Telecoms Interface Enclosure

## 4) Post Ener Pre Grid Code Cert
WINDFARM NAME (TLC) |  | Type | TSO | XX | MW | v1.0 |  | Post Energisation Signals and Controls Test
|  | RfG Type | D
EirGrid Signals, Command & Control Specification | [7 empty] | Simulated □/Real □ value tested | mA Range | Value Range | Comment
Post Energisation Signals and Controls (Pre Grid Code Check) Cert to be sent by ESBT to EirGrid (generator_testing@eirgrid.com)
ETIE Ref | Digital Input Signals (signals sent to EirGrid) |  |  |  |  | Provided by | TSO Pass-through to
| Double Point Status Indications | (each individual input identified separately for clarity)
Digital Input Signals from Sub Station to EirGrid
A1 | WINDFARM T121 WFPS 20 kV CB |  | open |  |  | WFPS | N/A | Real □
A2 | WINDFARM T121 WFPS 20 kV CB |  | closed |  |  | WFPS | N/A | Real □
A3 | WINDFARM Feeder 1 20 kV CB |  | open |  |  | WFPS | N/A | Real □
A4 | WINDFARM Feeder 1 20 kV CB |  | closed |  |  | WFPS | N/A | Real □
A5 | WINDFARM Feeder 2 20 kV CB |  | open |  |  | WFPS | N/A | Real □
A6 | WINDFARM Feeder 2 20 kV CB |  | closed |  |  | WFPS | N/A | Real □
A7 | WINDFARM Feeder 3 20 kV CB |  | open |  |  | WFPS | N/A | Real □
A8 | WINDFARM Feeder 3 20 kV CB |  | closed |  |  | WFPS | N/A | Real □
A9 | WINDFARM Feeder 4 20 kV CB |  | open |  |  | WFPS | N/A | Real □
A10 | WINDFARM Feeder 4 20 kV CB |  | closed |  |  | WFPS | N/A | Real □
A11 | WINDFARM Feeder 5 20 kV CB |  | open |  |  | WFPS | N/A | Real □
A12 | WINDFARM Feeder 5 20 kV CB |  | closed |  |  | WFPS | N/A | Real □
A13 | TSO Remote Control Enable Switch |  | off |  |  | WFPS | N/A | Real □
A14 | TSO Remote Control Enable Switch |  | on |  |  | WFPS | N/A | Real □
A15 | Black Start Shutdown Feedback |  | off |  |  | ESBN | N/A | Real □
A16 | Black Start Shutdown Feedback |  | on |  |  | ESBN | N/A | Real □
A17 | Reactive Device >5 Mvar 1 |  | off |  |  | WFPS | N/A | Real □
A18 | Reactive Device >5 Mvar 1 |  | on |  |  | WFPS | N/A | Real □
Digital Input Signals from WTG System to EirGrid
B1 | Active Power Control facility status (feedback) |  | off |  |  | WFPS | N/A | Real □
B2 | Active Power Control facility status (feedback) |  | on |  |  | WFPS | N/A | Real □
B3 | Frequency Response System Mode Status (feedback) |  | off |  |  | WFPS | N/A | Real □
B4 | Frequency Response System Mode Status (feedback) |  | on |  |  | WFPS | N/A | Real □
B5 | Frequency Response Curve (feedback) |  | Curve 1 |  |  | WFPS | N/A | Real □
B6 | Frequency Response Curve (feedback) |  | Curve 2 |  |  | WFPS | N/A | Real □
B7 | AVR (kV) Control facility status (feedback) |  | off |  |  | WFPS | N/A | Real □
B8 | AVR (kV) Control facility status (feedback) |  | on |  |  | WFPS | N/A | Real □
B9 | Q (Mvar) Control facility status (feedback) |  | off |  |  | WFPS | N/A | Real □
B10 | Q (Mvar) Control facility status (feedback) |  | on |  |  | WFPS | N/A | Real □
B11 | Power Factor (PF) Control facility status (feedback) |  | off |  |  | WFPS | N/A | Real □
B12 | Power Factor (PF) Control facility status (feedback) |  | on |  |  | WFPS | N/A | Real □
B13 | Emulated Inertia status (feedback) |  | off |  |  | WFPS | N/A | Real □
B14 | Emulated Inertia status (feedback) |  | on |  |  | WFPS | N/A | Real □
Recommended cable 15-pair, 15 x 2 x 0.6sqmm, Twisted-Pair (TP), stranded
ETIE Ref | Analogue Input Signals (to EirGrid) |  |  |  |  | Provided by | TSO Pass-through to
Analogue Input Signals from Sub Station to EirGrid
C1 | Active Power Output at LV side of Grid Connected Transformer | -10 to 0 to 10 | mA | #VALUE! | MW | WFPS | N/A | Real □
C2 | Reactive Power at LV side of Grid Connected Transformer | -10 to 0 to 10 | mA | #VALUE! | Mvar | WFPS | N/A | Real □
C3 | Voltage at LV side of Grid Connected Transformer | 0-10 | mA | 0 - 132 | kV | WFPS | N/A | Real □
Analogue Input Signals from WTG System to EirGrid
D1 | Available Active Power | 0-10 | mA | #VALUE! | MW | WFPS | N/A | Real □
D2 | Active Power Control Setpoint (feedback) | 0-10 | mA | #VALUE! | MW | WFPS | N/A | Real □
D3 | Voltage Control Setpoint (feedback) | 0-10 | mA | 99 - 132 | kV | WFPS | N/A | Real □
D4 | Mvar (Q) Control Setpoint (feedback) | -10 to 0 to 10 | mA | #VALUE! | Mvar | WFPS | N/A | Real □
D5 | Power Factor (PF) Control Setpoint (feedback) | -10 to 0 to 10 | mA | +/- 90 | degrees | WFPS | N/A | Real □
D6 | Frequency Droop Setting (feedback) | 0-10 | mA | 0-14 | % | WFPS | N/A | Real □
D7 | Transformer Tap Position | 0-10 | mA | 1 to 21 | Tap | WFPS | N/A | Real □
Analogue WTG Availability
D8 | %WTG not generating due to high wind | 0-10 | mA | 0-110 | % | WFPS | N/A | Real □
D9 | %WTG not generating due to low wind | 0-10 | mA | 0-110 | % | WFPS | N/A | Real □
D10 | Wind Farm Availability | 0-10 | mA | 0-110 | % | WFPS | N/A | Real □
Met 1 (if Registered Capacity >= 10 MW)
D11 | Emulated Inertia FFR availability | 0-10 | mA | 0-XX | MW | WFPS | N/A | Real □
D12 | Emulated Inertia POR availability | 0-10 | mA | 0-XX | MW | WFPS | N/A | Real □
D13 | Wind Speed 1 | 0-10 | mA | 0-70 | m/s | WFPS | N/A | Real □
D14 | Wind Direction 1 | 0-10 | mA | 0-360 | deg | WFPS | N/A | Real □
D15 | Air Temperature 1 | 0-10 | mA | -40-70 | C | WFPS | N/A | Real □
D16 | Air Pressure 1 | 0-10 | mA | 735-1060 | mBar | WFPS | N/A | Real □
Met N (if Registered Capacity >= 10 MW)
D17 | Wind Speed N | 0-10 | mA | 0-70 | m/s | WFPS | N/A | Real □
D18 | Wind Direction N | 0-10 | mA | 0-360 | deg | WFPS | N/A | Real □
D19 | Air Temperature N | 0-10 | mA | -40-70 | C | WFPS | N/A | Real □
D20 | Air Pressure N | 0-10 | mA | 735-1060 | mBar | WFPS | N/A | Real □
Recommended cable 25-pair cable: 25 x 2 x 0.6sqmm TP, stranded, individually screened pairs. Screens to be terminated by WFPS.
ETIE Ref | Digital Output Signals (from EirGrid) |  |  |  |  | Provided to | TSO Pass-through to
| Double Command Outputs | (each individual relay output identified separately)
Digital Output Signals from EirGrid to WTG System
E1 | Active Power Control facility status |  | off | pulse | 0.5 seconds | WFPS | N/A | Real □
E2 | Active Power Control facility status |  | on | pulse | 0.5 seconds | WFPS | N/A | Real □
E3 | Frequency Response System Mode Status |  | off | pulse | 0.5 seconds | WFPS | N/A | Real □
E4 | Frequency Response System Mode Status |  | on | pulse | 0.5 seconds | WFPS | N/A | Real □
E5 | Frequency Response Curve Select |  | Curve 1 | pulse | 0.5 seconds | WFPS | N/A | Real □
E6 | Frequency Response Curve Select |  | Curve 2 | pulse | 0.5 seconds | WFPS | N/A | Real □
E7 | Emulated Intertia |  | off | pulse | 0.5 seconds | WFPS | N/A | Real □
E8 | Emulated Intertia |  | on | pulse | 0.5 seconds | WFPS | N/A | Real □
Digital Output Signals from EirGrid to Sub Station
F1 | Blackstart Shutdown |  | off | pulse | 0.5 seconds | WFPS | N/A | Real □
F2 | Blackstart Shutdown |  | on | pulse | 0.5 seconds | WFPS | N/A | Real □
Strobe Enable Pulse
Digital Output Signals from EirGrid to WTG System
E9 | Digital Output Active Power Control Setpoint Enable |  |  | pulse | 0.5 seconds | WFPS | N/A | Real □
E10 | Digital Output Voltage Control (kV) Setpoint Enable |  |  | pulse | 0.5 seconds | WFPS | N/A | Real □
E11 | Digital Output Mvar Control (Q) Setpoint Enable |  |  | pulse | 0.5 seconds | WFPS | N/A | Real □
E12 | Digital Output Power Factor Control (PF) Setpoint Enable |  |  | pulse | 0.5 seconds | WFPS | N/A | Real □
E13 | Digital Output Frequency Droop Setting Enable |  |  | pulse | 0.5 seconds | WFPS | N/A | Real □
Single Command Outputs
E14 | Voltage Control facility status ON |  | on | pulse | 0.5 seconds | WFPS | N/A | Real □
E15 | Mvar (Q) Control Facility status ON |  | on | pulse | 0.5 seconds | WFPS | N/A | Real □
E16 | Power Factor (PF) Control facility status ON |  | on | pulse | 0.5 seconds | WFPS | N/A | Real □
Recommended Cable 15-pair Screened Cable : 15 x 2 x 0.6sqmm, Twisted-Pair ( TP).
ETIE Ref | Analogue Output Signals (from EirGrid) |  |  |  |  | Provided to | TSO Pass-through to
Analogue Output Signals from EirGrid to WTG System
G1 | Analogue Output Active Power Control Setpoint | 4 - 20 | mA | #VALUE! | MW | WFPS | N/A | Real □
G2 | Analogue Voltage Control Setpoint | 4 - 20 | mA | 99 - 132 | kV | WFPS | N/A | Real □
G3 | Analogue Mvar (Q) Control Setpoint | 4 - 20 | mA | #VALUE! | Mvar | WFPS | N/A | Real □
G4 | Analogue Power Factor (PF) Control Setpoint | 4 - 20 | mA | +/- 90 | degrees | WFPS | N/A | Real □
G5 | Frequency Droop Setting | 4 - 20 | mA | 0-14 | % | WFPS | N/A | Real □
Recommended cable 5-pair cable: 5 x 2 x 0.6sqmm TP, stranded, individually screened pairs. Screens to be terminated by WFPS.
| Confirm the source of the MET signals e.g. from MET mast or from WTGs | What is the last voltage control mode and setpoint issued to the WFPS? (Default MVAr control mode with 0 MVAr set point)
| Wind Speed source: |  |  |  |  | WFPS Name |  | 0
| Wind Direction source: |  |  |  |  | WFPS Signature
| Air Temperature source: |  |  |  |  | EMS Name
| Air Pressure source: |  |  |  |  | EMS Signature
| NOTE: Non operable WFPS signals will result in rescheduling for re-commissioning and require another Joint Signals Test Cert to be performed. |  |  |  |  | ESB Telecoms Name / Position |  | ESBTS Team
| Note: That for the duration of the Post Energization Test, there should be NO external influencing factors |  |  |  |  | ESB Telecoms Signature
| Information may be sent to by email: generator_testing@eirgrid.com, Fax: +353 (0)1 661 5375 or Post to: System Support, EirGrid, The Oval, 160 Shelbourne Road, Ballsbridge, Dublin 4 |  |  |  |  | Date
Note on A6: EirGrid Telecoms Interface Enclosure

## ETIE
EirGrid Telecoms Interface Enclosure (ETIE)
Typical EirGrid RTU cabinet with integrated ETI and GPS clock 2.0m x 0.8m x 0.6m (rear access not required).
Note: This is for a typical installation and may vary from project to project. Any queries should be directed to generator_testing@eirgrid.com or esbts.scada.services@esb.ie
ETIE General Description
There will be four rows of terminals labelled Row 1, 2, 3, 4 as shown in the Layout drawing and Photograph above
Trunking shall be separated into WFPS and EirGrid Telecoms trunking.
EirGrid Telecoms cabling to be in EirGrid Telecoms designated trunking only
WFPS cabling to be in WFPS designated trunking only
Access to terminals will be as follows:
Upper side to be used for EirGrid Telecoms use only
Lower side to be used for WFPS use only
Isolating link to sever all connection between the WFPS connection and EirGrid Telecoms connection
Command terminals to be covered with a Perspex cover and labelled "DO NOT ENERGISE"
Earthing of cabinet to be completed in accordance with 35 sq mm earth cable to EirGrid Telecoms earth bar

## ETIE Layout
Designation: Indications/Signals |  | ETIE Ref | ETIE ROW 1
POSITIVE 24V or 48V DC DOUBLE POINT INDICATION |  |  | +
WINDFARM T121 WFPS 20 kV CB | open | A1 | 1
WINDFARM T121 WFPS 20 kV CB | closed | A2 | 2
WINDFARM Feeder 1 20 kV CB | open | A3 | 3
WINDFARM Feeder 1 20 kV CB | closed | A4 | 4
WINDFARM Feeder 2 20 kV CB | open | A5 | 5
WINDFARM Feeder 2 20 kV CB | closed | A6 | 6
WINDFARM Feeder 3 20 kV CB | open | A7 | 7
WINDFARM Feeder 3 20 kV CB | closed | A8 | 8
WINDFARM Feeder 4 20 kV CB | open | A9 | 9
WINDFARM Feeder 4 20 kV CB | closed | A10 | 10
WINDFARM Feeder 5 20 kV CB | open | A11 | 11
WINDFARM Feeder 5 20 kV CB | closed | A12 | 12
TSO Remote Control Enable Switch | off | A13 | 13
TSO Remote Control Enable Switch | on | A14 | 14
Black Start Shutdown Feedback | off | A15 | 15
Black Start Shutdown Feedback | on | A16 | 16
Reactive Device >5 Mvar 1 | off | A17 | 17
Reactive Device >5 Mvar 1 | on | A18 | 18
Active Power Control facility status (feedback) | off | B1 | 19
Active Power Control facility status (feedback) | on | B2 | 20
Frequency Response System Mode Status (feedback) | off | B3 | 21
Frequency Response System Mode Status (feedback) | on | B4 | 22
Frequency Response Curve (feedback) | Curve 1 | B5 | 23
Frequency Response Curve (feedback) | Curve 2 | B6 | 24
AVR (kV) Control facility status (feedback) | off | B7 | 25
AVR (kV) Control facility status (feedback) | on | B8 | 26
Q (Mvar) Control facility status (feedback) | off | B9 | 27
Q (Mvar) Control facility status (feedback) | on | B10 | 28
Power Factor (PF) Control facility status (feedback) | off | B11 | 29
Power Factor (PF) Control facility status (feedback) | on | B12 | 30
Emulated Inertia status (feedback) | off | B13 | 31
Emulated Inertia status (feedback) | on | B14 | 32
33
34
35
36
37
38
39
40
POSITIVE 24V or 48V DC SINGLE POINT INDICATION |  |  | +
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
Designation: Measurands | Polarity | ETIE Ref | ETIE ROW 2
Active Power Output at LV side of Grid Connected Transformer | + | C1 | 1
Active Power Output at LV side of Grid Connected Transformer | - | C1 | 2
Reactive Power at LV side of Grid Connected Transformer | + | C2 | 3
Reactive Power at LV side of Grid Connected Transformer | - | C2 | 4
Voltage at LV side of Grid Connected Transformer | + | C3 | 5
Voltage at LV side of Grid Connected Transformer | - | C3 | 6
Available Active Power | + | D1 | 7
Available Active Power | - | D1 | 8
Active Power Control Setpoint (feedback) | + | D2 | 9
Active Power Control Setpoint (feedback) | - | D2 | 10
Voltage Control Setpoint (feedback) | + | D3 | 11
Voltage Control Setpoint (feedback) | - | D3 | 12
Mvar (Q) Control Setpoint (feedback) | + | D4 | 13
Mvar (Q) Control Setpoint (feedback) | - | D4 | 14
Power Factor (PF) Control Setpoint (feedback) | + | D5 | 15
Power Factor (PF) Control Setpoint (feedback) | - | D5 | 16
Frequency Droop Setting (feedback) | + | D6 | 17
Frequency Droop Setting (feedback) | - | D6 | 18
Transformer Tap Position | + | D7 | 19
Transformer Tap Position | - | D7 | 20
%WTG not generating due to high wind | + | D8 | 21
%WTG not generating due to high wind | - | D8 | 22
%WTG not generating due to low wind | + | D9 | 23
%WTG not generating due to low wind | - | D9 | 24
Wind Farm Availability | + | D10 | 25
Wind Farm Availability | - | D10 | 26
Emulated Inertia FFR availability | + | D11 | 27
Emulated Inertia FFR availability | - | D11 | 28
Emulated Inertia POR availability | + | D12 | 29
Emulated Inertia POR availability | - | D12 | 30
Wind Speed 1 | + | D13 | 31
Wind Speed 1 | - | D13 | 32
Wind Direction 1 | + | D14 | 33
Wind Direction 1 | - | D14 | 34
Air Temperature 1 | + | D15 | 35
Air Temperature 1 | - | D15 | 36
Air Pressure 1 | + | D16 | 37
Air Pressure 1 | - | D16 | 38
Wind Speed N | + | D17 | 39
Wind Speed N | - | D17 | 40
Wind Direction N | + | D18 | 41
Wind Direction N | - | D18 | 42
Air Temperature N | + | D19 | 43
Air Temperature N | - | D19 | 44
Air Pressure N | + | D20 | 45
Air Pressure N | - | D20 | 46
47
48
49
50
51
52
53
54
Designation: Commands | Polarity | ETIE Ref | ETIE ROW 3
Analogue Output Active Power Control Setpoint | + | G1 | 1
Analogue Output Active Power Control Setpoint | - | G1 | 2
Analogue Voltage Control Setpoint | + | G2 | 3
Analogue Voltage Control Setpoint | - | G2 | 4
Analogue Mvar (Q) Control Setpoint | + | G3 | 5
Analogue Mvar (Q) Control Setpoint | - | G3 | 6
Analogue Power Factor (PF) Control Setpoint | + | G4 | 7
Analogue Power Factor (PF) Control Setpoint | - | G4 | 8
Frequency Droop Setting | + | G5 | 9
Frequency Droop Setting | - | G5 | 10
11
12
13
14
15
16
17
18
Designation: Controls |  | ETIE Ref | ETIE ROW 4
Active Power Control facility status | off | E1 | 1
Command Negative |  |  | 2
Active Power Control facility status | on | E2 | 3
Frequency Response System Mode Status | off | E3 | 4
Command Negative |  |  | 5
Frequency Response System Mode Status | on | E4 | 6
Frequency Response Curve Select | Curve 1 | E5 | 7
Command Negative |  |  | 8
Frequency Response Curve Select | Curve 2 | E6 | 9
Emulated Intertia | off | E7 | 10
Command Negative |  |  | 11
Emulated Intertia | on | E8 | 12
Blackstart Shutdown | off | F1 | 13
Command Negative |  |  | 14
Blackstart Shutdown | on | F2 | 15
Command Output |  |  | 16
Command Negative |  |  | 17
Command Output |  |  | 18
Command Output |  |  | 19
Command Negative |  |  | 20
Command Output |  |  | 21
Command Output |  |  | 22
Command Negative |  |  | 23
Command Output |  |  | 24
Command Output |  |  | 25
Command Negative |  |  | 26
Command Output |  |  | 27
Command Output |  |  | 28
Command Negative |  |  | 29
Command Output |  |  | 30
Single Controls |  |  | +
31
32
33
34
35
36
Voltage Control facility status ON |  | E14 | 37
|  | E14 | 38
Mvar (Q) Control Facility status ON |  | E15 | 39
|  | E15 | 40
Power Factor (PF) Control facility status ON |  | E16 | 41
|  | E16 | 42
Digital Output Active Power Control Setpoint Enable |  | E9 | 43
|  | E9 | 44
Digital Output Voltage Control (kV) Setpoint Enable |  | E10 | 45
|  | E10 | 46
Digital Output Mvar Control (Q) Setpoint Enable |  | E11 | 47
|  | E11 | 48
Digital Output Power Factor Control (PF) Setpoint Enable |  | E12 | 49
|  | E12 | 50
Digital Output Frequency Droop Setting Enable |  | E13 | 51
|  | E13 | 52
53
54
55
56
57
58
59
60
Note on D2: There should be no Gaps between the individual Wiring references for Row 1, 2 and 4
Note on D68: Administrator: Administrator: There should be no Gaps between the individual Wiring references for Row 1, 2 and 4
Note on D123: Administrator: There is a gap between the off / on commands for command negative
Note on D142: Administrator: There should be no Gaps between the individual Wiring references for Row 1, 2 and 4

## Freq,Ramping,Voltage Settings
Frequency, Ramp Rate and Voltage Settings to be implemented in Wind Farm Control System
Definitions:
| AAP | Available Active Power
| DMOL | Designed Minimum Operating Level
| APC | Active Power Control
Frequency Response Mode On | [5 empty] | Frequency Response Diagrams
Curve 1: Wind Following Mode (RfG Limited Frequency Sensitive Mode)
|  |  | Transmission System Frequency f (Hz) |  | Required Active Power Output
|  |  | f < 48 |  | 100% of AAP
|  | FA | 48 | PA | 100% of AAP
|  | Under Frequency Response | 48 < f < 49.8 |  | 100% of AAP
|  | FB | f = 49.8 | PB | 100% of AAP
|  | +/-0.2Hz Deadband | 49.8 < f < 50.2 |  | 100% of AAP
|  | FC | f = 50.2 | PC | 100% of AAP
|  | Over Frequency Response | 50.2 < f < 51.9 |  | AAP + ∆MW2
|  | FD | f = 51.9 | PD | Minimum of: AAP and DMOL
|  | FE | f = 52 | PE | 0%3
|  |  | f > 52 |  | 0%3
Curve 1: Active Power Control Mode (RfG Frequency Sensitive Mode)
|  |  | Transmission System Frequency f (Hz) |  | Required Active Power Output
|  |  | f < 48 |  | 100% of AAP
|  | FA | f = 48 | PA | 100% of AAP
|  | Under Frequency Response | 48 < f < 49.985 |  | Minimum of: APC Setpoint + ∆MW and AAP
|  | FB | f = 49.985 | PB | Minimum of: APC Setpoint and AAP
|  | +/-0.015Hz Deadband | 49.985 < f < 50.015 |  | Minimum of: APC Setpoint and AAP
|  | FC | f = 50.015 | PC | Minimum of: APC Setpoint and AAP
|  | Over Frequency Response | 50.015 < f < 51.9 |  | Minimum of: APC Setpoint + ∆MW and AAP + ∆MW1, 2
|  | FD | f = 51.9 | PD | Minimum of: APC Setpoint and AAP and DMOL
|  | FE | f = 52 | PE | 0%3
|  |  | f > 52 |  | 0%3
Curve 2: Wind Following Mode
|  |  | Transmission System Frequency f (Hz) |  | Required Active Power Output
|  |  | f <49.3 |  | 100% of AAP
|  | FA | f = 49.3 | PA | 100% of AAP
|  | Under Frequency Response | 49.3 < f < 49.985 |  | 95% of Available Active Power + ∆MW
|  | FB | f = 49.985 | PB | 95% of Available Active Power. This is = to 5% Reserve.
|  | +/-0.015Hz Deadband | 49.985 < f < 50.015 |  | 95% of Available Active Power. This is = to 5% Reserve.
|  | FC | f = 50.015 | PC | 95% of Available Active Power. This is = to 5% Reserve.
|  | Over Frequency Response | 50.015 < f < 51.9 |  | 95% of AAP + ∆MW2
|  | FD | f = 51.9 | PD | Minimum of: AAP and DMOL
|  | FE | f = 52 | PE | 0%3
|  |  | f > 52 |  | 0%3
Curve 2: Active Power Control Mode
|  |  | Transmission System Frequency f (Hz) |  | Required Active Power Output
|  |  | f < 49.3 |  | 100% of AAP
|  | FA | f = 49.3 | PA | 100% of AAP
|  | Under Frequency Response | 49.3 < f < 49.985 |  | Minimum of: APC Setpoint + ∆MW and 95% of AAP + ∆MW
|  | FB | f = 49.985 | PB | Minimum of: APC Setpoint and 95% of AAP
|  | +/-0.015Hz Deadband | 49.985 < f < 50.015 |  | Minimum of: APC Setpoint and 95% of AAP
|  | FC | f = 50.015 | PC | Minimum of: APC Setpoint and 95% of AAP
|  | Over Frequency Response | 50.015 < f < 51.9 |  | Minimum of: APC Setpoint + ∆MW and 95% of AAP + ∆MW1, 2
|  | FD | f = 51.9 | PD | Minimum of: APC Setpoint and AAP and DMOL
|  | FE | f = 52 | PE | 0%3
|  |  | f > 52 |  | 0%3
Minimum reserve level in Curve 2 is 5% of Available Active Power, not lower than DMOL (settable between DMOL and 100%)
Frequency Response Mode OFF
Curve 1 and Curve 2: Wind Following Mode
|  |  | Transmission System Frequency (Hz) |  | Required Active Power Output
|  |  | 47.5 ≤ f ≥ 52 | No governor action | 100% of AAP
Curve 1 and Curve 2: Active Power Control Mode
|  |  | Transmission System Frequency (Hz) |  | Required Active Power Output
|  |  | 47.5 ≤ f ≥ 52 | No governor action | Minimum of: AAP and APC Setpoint
1 APC Setpoint + ∆MW shall have a lower limit of the minimum of: APC Setpoint and DMOL.
2 (95% of) AAP + ∆MW shall have a lower limit of the minimum of AAP and DMOL
3 Any WTG which has disconnected due to high frequency shall be brought back on load as fast as technically feasible, provided the Frequency has fallen below 50.2Hz.
DMOL shall not be greater than 12% of Registered Capacity
If AAP < DMOL and f < FE, maximise output
Ramp Rates:
|  | Mode | Rate | Priority | Comment
|  | Frequency Response | As fast as technically possible. 60% of its expected Active Power response within 5 seconds 100% of its expected Active Power response within 15 seconds. | 1
|  | Active Power Dispatch | 20% of Registered Capacity per Minute | 2 | Settable between: 1-100% Registered Capacity per Minute
|  | Wind Following | 20% of Registered Capacity per Minute | 3 | Settable between: 1-100% Registered Capacity per Minute
Frequency Droop:
|  | Frequency Droop | Droop Calculation | Comment
|  | 4% |  | Settable between: 2-12%, online
Rate of Change of Frequency:
If possible, ROCOF should be disabled on Transmission System-connected Windfarms. If this is not possible, ROCOF should be set to max that machine is capable of. Under no circumstances should ROCOF be set to less than 0.5 Hz/s
Proposed Modification to Grid Code. (Ref#MPID 229).
Voltage Regulation System Slope Setting
|  | Voltage System Slope | Voltage Calculation | Comment
|  | 4% |  | 90% of steady State Reactive Power response within 1 second including transition from maximum Mvar production to maximum Mvar absorption or vice-versa.
Note. Frequency Response settings have been updated to clarify expected performance below DMOL - per feedback from industry. Changes are highlighted in red.
Note. Fd and Fe have been updated, along with clarification of minimum reserve held. Changes are highlighted in red.

## Turbine Protection Settings
Recommended Wind Farm Power Station (WFPS) Turbine Protection Settings to be applied by WFPS
| Underfrequency stage 1 Setpoint | f< | 47.5 Hz | If only two stages available for underfrequency on relay, use stage 2 and stage 3
| Underfrequency stage 1 time delay | t< | 3600 s
| Underfrequency stage 2 Setpoint | f<< | 47.4 Hz
| Underfrequency stage 2 time delay | t<< | 20 s
| Underfrequency stage 3 Setpoint | f<<< | 46.9 Hz
| Underfrequency stage 3 time delay | t<<< | 1 s
| Overfrequency stage 1 Setpoint | f> | 52Hz
| Overfrequency stage 1 time delay | t> | 3600 s
| Overfrequency stage 2 Setpoint | f>> | 52.1 Hz
| Overfrequency stage 2 time delay | t>> | 1 s
| Rate of Change of Frequency setpoint | df/dt | Max | If possible, ROCOF should be disabled on Transmission System-connected Windfarms. If this is not possible, ROCOF should be set to max that machine is capable of. Under no circumstances should ROCOF be set to less than 1 Hz/s over 500 ms
| Rate of Change of Frequency delay | t | Max
| Undervoltage stage 1 Setpoint | U< | 0.89 pu
| Undervoltage stage 1 time delay | t< | 3 s
| Undervoltage stage 2 Setpoint | U<< | 0.14 pu
| Undervoltage stage 2 time delay | t<< | 0.625 s
| Overvoltage stage 1 Setpoint | U> | 1.11 pu
| Overvoltage stage 1 time delay | t> | 60 s | This is the minimum time delay we would recommend. If the plant can operate at this voltage for longer periods, then a longer time delay (at the discretion of the WFPS) should be implemented.
| Overvoltage stage 2 Setpoint | U>> | 1.2 pu
| Overvoltage stage 2 time delay | t>> | 15 s | This is the minimum time delay we would recommend. If the plant can operate at this voltage for longer periods, then a longer time delay (at the discretion of the WFPS) should be implemented.
| Fault Ride Through Events | N | N/A | Trip & Lockout Settings. i.e No. of events within specified time period. Confirm if time period is rolling. NB. Lockout is not recommended by EirGrid.
| Fault Ride Though Time Period (Rolling) | t | N/A

## Blackstart Shutdown
Testing Requirements for Blackstart Shutdown, per Functional Spec XDS-GFS-21-001-R1 dated 07/09/2012 and associated schematic drawing XDS-DELS-00-005
Initial Conditions | T121 110 kV CB | CLOSED
| T121 WFPS 20 kV CB | CLOSED
| T121 110 kV cubicle Sub Remote Control Switch | OFF
| EirGrid Remote Control Enable Switch | ON
Action | NCC enable Blackstart Shutdown command | Time:
Outcome | T121 110 kV CB: Remains Closed
T121 WFPS 20 kV CB: Remains Closed
Blue Alert Lamp: Remains unlit
Additional Notes
Initial Conditions | T121 110 kV CB | CLOSED
| T121 WFPS 20 kV CB | CLOSED
| T121 110 kV cubicle Sub Remote Control Switch | ON
| EirGrid Remote Control Enable Switch | OFF
Action | NCC enable Blackstart Shutdown command | Time:
Outcome | T121 110 kV CB: Opens
T121 WFPS 20 kV CB: Remains Closed
Blue Alert Lamp: Lamp illuminates
Additional Notes | 20 kV CB must not be tripped by BSSD with RCES off. Tripping under LOM protection etc. may occur
Initial Conditions | T121 110 kV CB | OPEN
| T121 WFPS 20 kV CB | OPEN
| T121 110 kV cubicle Sub Remote Control Switch | ON
| EirGrid Remote Control Enable Switch | ON
| Blackstart Shutdown command | ON
Action | WFPS attempt to close WFPS 20 kV CB at mimic panel | Time:
Outcome | T121 110 kV CB: Remains Open
T121 WFPS 20 kV CB: Remains Open
Blue Alert Lamp: Remains Illuminated
Additional Notes | WFPS must clear all alarms that would inhibit 20 kV CB from being closed (LOM protection, etc.) before attempting to close 20 kV CB
Initial Conditions | T121 110 kV CB | OPEN
| T121 WFPS 20 kV CB | OPEN
| T121 110 kV cubicle Sub Remote Control Switch | ON
| EirGrid Remote Control Enable Switch | ON
| Blackstart Shutdown command | ON
Action | WFPS turn EirGrid Remote Control Enable Switch OFF | Time:
Outcome | T121 110 kV CB: Remains Open
T121 WFPS 20 kV CB: Remains Open
Blue Alert Lamp: Remains Illuminated
Additional Notes
Initial Conditions | T121 110 kV CB | OPEN
| T121 WFPS 20 kV CB | OPEN
| T121 110 kV cubicle Sub Remote Control Switch | ON
| EirGrid Remote Control Enable Switch | OFF
| Blackstart Shutdown command | ON
Action | WFPS attempt to close WFPS 20 kV CB at mimic panel | Time:
Outcome | T121 110 kV CB: Remains Open
T121 WFPS 20 kV CB: Remains Open
Blue Alert Lamp: Remains Illuminated
Additional Notes

## Test Schedule and Templates
Grid Code Compliance Test Schedule and Test Procedure templates
SCHEDULE OF GRID CODE COMPLIANCE TESTS
http://www.eirgridgroup.com/site-files/library/EirGrid/WFPS_Schedule_of_GridCodeComplianceTests.xlsx
Test Procedure Templates | UPDATE!!
http://www.eirgridgroup.com/site-files/library/EirGrid/WFPS-Active-Power-Control-Test-Procedure.docx
http://www.eirgridgroup.com/site-files/library/EirGrid/WFPS-Black-Start-Shutdown-Test-Procedure.docx
http://www.eirgridgroup.com/site-files/library/EirGrid/WFPS_Test-Procedure-Frequency-Response.docx
http://www.eirgridgroup.com/site-files/library/EirGrid/WFPS%20Test%20Procedure%20Reactive%20Power%20Control.docx
http://www.eirgridgroup.com/site-files/library/EirGrid/WFPS-Reactive-Power-Capability-Test-Procedure.docx
http://www.eirgridgroup.com/site-files/library/EirGrid/WFPS-Site-Survey-Procedure.docx