## Cover Sheet
CDGU Rocof Calculations Workbook
Disclaimer information can be found at: http://www.eirgridgroup.com/legal/

## Droop Calculations_EirGrid
Step | Frequency deviation in Hz | Initial MW | Final MW | MW change | Expected MW | Delta MW | Calculated Droop in % | Expected droop in % | Delta Droop | Comment | Static Data
Min load -0.5 Hz Ramp at 1 Hz/Second | -0.5 |  |  | 0 | 25 | -25 | #DIV/0! | 4% | #DIV/0! |  |  | Registered Capacity | 100 | MW
Min load +0.5 Hz Ramp at 1 Hz/Second | 0.5 |  |  | 0 | -25 | 25 | #DIV/0! | 4% | #DIV/0! |  |  | Expected Droop | 4% | %
75% -0.5 Hz Ramp at 1 Hz/Second | -0.5 |  |  | 0 | 25 | -25 | #DIV/0! | 4% | #DIV/0! |  |  | Nominal frequency | 50 | Hz
75% +0.5 Hz Ramp at 1 Hz/Second | 0.5 |  |  | 0 | -25 | 25 | #DIV/0! | 4% | #DIV/0!
90% -0.5 Hz Ramp at 1 Hz/Second | -0.5 |  |  | 0 | 25 | -25 | #DIV/0! | 4% | #DIV/0! |  | Cells in orange are for user input
100% +0.5 Hz Ramp at 1 Hz/Second | 0.5 |  |  | 0 | -25 | 25 | #DIV/0! | 4% | #DIV/0! |  | Cells in white are calculated based on static data above and on the frequency injection

## Droop Calculations_SONI
Step | Frequency deviation in Hz | Initial MW | Final MW | MW change | Expected MW | Delta MW | Calculated Droop in % | Expected droop in % | Delta Droop | Comment | Static Data
100% -0.5 Hz Ramp at 2 Hz/s | -0.5 |  |  | 0 | 25 | -25 | #DIV/0! | 4% | #DIV/0! |  |  | Registered Capacity | 100 | MW
100% +0.5 Hz Ramp at 2 Hz/s | 0.5 |  |  | 0 | -25 | 25 | #DIV/0! | 4% | #DIV/0! |  |  | Expected Droop | 4% | %
75% -0.5 Hz Ramp at 1 Hz/s, Hold for 1s, +1 Hz Ramp at 1 Hz/s | -0.5 |  |  | 0 | 25 | -25 | #DIV/0! | 4% | #DIV/0! |  |  | Nominal frequency | 50 | Hz
| 1 |  |  | 0 | -50 | 50 | #DIV/0! | 4% | #DIV/0!
75% -0.5 Hz Ramp at 2 Hz/s | 0.5 |  |  | 0 | -25 | 25 | #DIV/0! | 4% | #DIV/0!
75% +0.5 Hz Ramp at 1 Hz/s, Hold for 1s, -1 Hz Ramp at 1 Hz/s | 0.5 |  |  | 0 | -25 | 25 | #DIV/0! | 4% | #DIV/0! |  | 1. Cells in orange are for user input 2. Cells in white are calculated based on static data above and on the frequency injection
| -1 |  |  | 0 | 50 | -50 | #DIV/0! | 4% | #DIV/0!
75% +0.5 Hz Ramp at 2 Hz/s | 0.5 |  |  | 0 | -25 | 25 | #DIV/0! | 4% | #DIV/0!
Min load -0.5 Hz Ramp at 2 Hz/s | -0.5 |  |  | 0 | 25 | -25 | #DIV/0! | 4% | #DIV/0!
Min load +0.5 Hz Ramp at 2 Hz/s | 0.5 |  |  | 0 | -25 | 25 | #DIV/0! | 4% | #DIV/0!