## Process
IMPORTANT - PLEASE READ
A Test request form must be submitted for any testing, changes to WFPS characteristics, or software or hardware upgrades.
Test Request Process
The WFPS completes the following:
1. Fill in all details highlighted in - |  | YELLOW
2. Timeline in column A should be amended/extended as appropriate.
3. Available MW in column B should be estimated based on wind forecast.
4. Submit a separate tab for each day.
5. This request form must be submitted to generator_testing@eirgrid.com by 10am, 2 days prior to commencement.
6. Follow the update process.
7. If the update carries risk of unintended operation or will affect reactive power control, response or capability, the WFPS shall carry out the update offline.
8. Signal Checks or Grid Code testing may be required following software or hardware updates. E.g. Controller replacement will lead to post-energisation signals and control check and Grid Code Compliance Testing.
Before any modification to a Generator Unit/WFPS takes place the User must inform the TSO. Modifications which are made without informing the TSO which alter the technical capabilities, flexibilities or limitations of the Unit either positively or negatively with respect to the requirements of the Grid Code may result in the withdrawal of a valid Operational Certificate or Operational Readiness Confirmation. All Users are obliged to inform the TSO of any changes to the technical capabilities, flexibilities or limitations of their Unit due to ageing of plant or apparatus.

## Within Day Profile (Test Date1)
WFPS Load Profile Request Form
Time | Available MW | MW | MVAr | Available for MW Dispatch | Available for Mvar Dispatch | Comment | UNIT NAME | (Windfarm Name)
8:00 | XX | As Required | As Required | Y | Y |  | Registered Capacity (MW) | XX
8:05 | XX | As Required | As Required | Y | Y |  | Test Date | xx/xx/20xx
8:10 | XX | As Required | As Required | Y | Y |  | Risk of Unitended Operation? | YES/NO
8:15 | XX | As Required | As Required | Y | Y |  | Will WFPS be Offline for Update? | YES/NO
8:20 | XX | As Required | As Required | Y | Y |  | NCC Operator Signals/Commands required? | YES/NO
8:25 | XX | As Required | As Required | Y | Y |  | If NCC interaction required, outline extent; e.g. none e.g. 10 Setpoints required over 30minute period e.g. Turn frequency response on and change curve after 1 Hour.
8:30 | XX | As Required | As Required | Y | Y
8:35 | XX | As Required | As Required | Y | Y
8:40 | XX | As Required | As Required | Y | Y
8:45 | XX | As Required | As Required | Y | Y
8:50 | XX | As Required | As Required | Y | Y |  | Purpose & Description of Test or Software/Hardware Update
8:55 | XX | As Required | As Required | Y | Y |  | The WFPS will be Uncontrollable/Controllable. Explain reason for test/ impact of software or Hardware update; e.g. Improve ramp rate during frequency response e.g. test bumpless transfer
9:00 | XX | 0 | 0 | N | N
9:05 | XX | 0 | 0 | N | N
9:10 | XX | 0 | 0 | N | N
9:15 | XX | 0 | 0 | N | N |  | Contact Name (person responsible for the software update and capable of adjusting output of WFPS if required by NCC) | Mobile | Position/Role
9:20 | XX | 0 | 0 | N | N
9:25 | XX | 0 | 0 | N | N
9:30 | XX | 0 | 0 | N | N
9:35 | XX | 0 | 0 | N | N
9:40 | XX | 0 | 0 | N | N
9:45 | XX | 0 | 0 | N | N
9:50 | XX | 0 | 0 | N | N
9:55 | XX | 0 | 0 | N | N
10:00 | XX | 0 | 0 | N | N
10:05 | XX | 0 | 0 | N | N
10:10 | XX | 0 | 0 | N | N
10:15 | XX | 0 | 0 | N | N
10:20 | XX | 0 | 0 | N | N
10:25 | XX | 0 | 0 | N | N
10:30 | XX | 0 | 0 | N | N
10:35 | XX | 0 | 0 | N | N
10:40 | XX | 0 | 0 | N | N
10:45 | XX | 0 | 0 | N | N
10:50 | XX | As Required | As Required | Y | Y
10:55 | XX | As Required | As Required | Y | Y
11:00 | XX | As Required | As Required | Y | Y
11:05 | XX | As Required | As Required | Y | Y
11:10 | XX | As Required | As Required | Y | Y
11:15 | XX | As Required | As Required | Y | Y
11:20 | XX | As Required | As Required | Y | Y
11:25 | XX | As Required | As Required | Y | Y
11:30 | XX | As Required | As Required | Y | Y
11:35 | XX | As Required | As Required | Y | Y
11:40 | XX | As Required | As Required | Y | Y
11:45 | XX | As Required | As Required | Y | Y
11:50 | XX | As Required | As Required | Y | Y
Note on B6: Based on best available forecast
Note on I6: PLEASE ENTER THE UNIT NAME AND EMS NAME
Note on H7: Lesser of Installed Capacity and MEC. If a capacity limit is in place then it should be reflected here.

## Update Process
Software/Hardware Update Process
Step | Online Updates | Step | Offline Updates | Completed | No
| BEFORE WORKS |  | BEFORE WORKS
1.1 | On the day of update, the WFPS contacts NCC, notifies them of the works, requests permission to be moved into Generator Testing category in the Wind Dispatch Tool, and agrees logistics to proceed (time, any additional steps as required). | 1.1 | On the day of update, the WFPS contacts NCC, notifies them of the update, requests permission to be moved into Generator Testing category in the Wind Dispatch Tool, and agrees logistics to proceed (time, any additional steps as required).
|  | 1.2 | In agreement with NCC, WFPS shuts down all WTGs. |  | N/A
| ON COMPLETION OF WORKS |  | ON COMPLETION OF WORKS
2.1 | Following completion of the update, the WFPS contacts NCC, notifies them that the work is completed, and confirms the following with NCC: | 2.1 | Following completion of the update, the WFPS shall contact NCC, notifies them that the work is completed and requests permission to start up e.g. 3 WTGs, such that NCC can test active and reactive power control with minimal risk to the system.
| AAP of the WFPS | 2.2 | NCC shall change the kV set-point by 1 kV and confirm that the set-point feedback is correct and the Mvar output is appropriate.
| MW Output of the WFPS | 2.3 | NCC shall set the kV set-point to a value appropriate to system conditions.
| Active Power Control is OFF | 2.4 | In agreement with NCC, WFPS shall start additional WTGs and repeat steps 2.2 and 2.3 at varying load levels e.g. 50% and 100% of WTGs online
| Frequency Response ON | 2.5 | WFPS shall confirm the follwing with NCC:
| Frequency Curve 1 is ON |  | AAP of the WFPS
| Reactive Power Control Mode (AVR, PF, Mvar) |  | MW Output of the WFPS
| Grid Connected Transformer Tap Position |  | Frequency Response is ON
| On Load Tap Changer is in Automatic Mode |  | Reactive Power Control Mode (AVR)
| System Voltage |  | Grid Connected Transformer Tap Position
| WFPS Voltage slope setting = 4% |  | On Load Tap Changer is in Automatic Mode
| Mvar Export |  | System Voltage
2.2 | NCC shall issue a constraint e.g. 50% of the current output. |  | Voltage slope setting = 4%
2.3 | NCC shall remove the contstraint. |  | Mvar Export
2.4 | WFPS Notifies NCC, requests to be removed from Generator Testing mode and informs them that the test is complete. | 2.5 | NCC shall issue a constraint e.g. 75% of the current output.
|  | 2.6 | NCC shall remove the contstraint.
|  | 2.7 | WFPS Notifies NCC, requests to be removed from Generator Testing mode and informs them that the test is complete.